| Sr. No. | Clause No. and Details | Bidder's Query/Comment | Reply from POWERGRID |
| --- | --- | --- | --- |
|  | ITB/BDS | Details of the Site Visit Schedule is not available in the tender documents. Request you to please provide Site Visit Schedule arranged by Employer. | The Bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines, inputs, conditions and circumstances and factors that may have any effect on his Bid. |
|  | BDS ITB 7.4 | As per the clause Pre-Bid meeting is scheduled on 28.07.2022 and details of the suitable video conferencing platform shall be indicated on the e-procurement portal. However, details of the same is not on the portal. Please provide. | Please refer POWERGRID letter dated 27.07.2022 regarding change of date of Prebid meeting. |
|  | General | Co-ordinates for Terminal and Angle Points for Transmission line is not provided in the tender documents. Request you to please provide Co-ordinates. | The Preliminary Survey report for 400kV D/C Lessos-Loosuk Transmission Project along with the KMZ file for coordinates for the terminal and Angle Points of line has been enclosed as Appendix-A-I & A-II, respectively. The Survey Report has been provided in good faith, and on best endeavour basis. Employer does not warranty, express or implied, or accept any responsibility or liability, whatsoever, in respect of any statements or omissions made in the Survey Report, or the accuracy, completeness or reliability of information contained therein, and shall incur no liability under any law, statute, rules or regulations as to the accuracy, reliability or completeness of such Survey Report, even if any loss or damage is caused to the Bidders by any act or omission on their part. Bidders shall make best efforts and carry out its own due diligence upon survey report provided by Employer and shall consider all possible techno-commercial factors before submission of Bid. Bidders may also visit the route of the Transmission Lines associated with the Project and the surrounding areas and obtain / verify all information which they deem fit and necessary for the preparation of their Bid. Bidders may also carry out required surveys and field investigation for submission of their Bid. |
|  | Design – Basic Wind Velocity | As per Volume II, Section-I A, (Standard) Scope of Work, Clause no. 5 - Service Conditions, page no. 9 of 9, Basic wind velocity is mentioned as 46 m/s. We presume that, it is the basic design reference wind speed of 46 m/s as mean value of wind during 10 min period at a level of 10m above ground. Please confirm if our understanding is correct. | Bidders understanding is correct. |
|  | Temperature for Conductor and OPGW/Ground Wire | In the tender document, Basic conductor, and OPGW/ground-wire temperature such as minimum temperature, everyday temperature and maximum temperature are not furnished. Request you to kindly furnish the same for our ready reference. | - Please refer following clauses regarding temperature for conductor & EW/ OPGW - (i) Clause no. 1.4.10 of Section IVA for Conductor and Earthwire - (ii) Clause no. 2.1.2.3 of Section X for OPGW - Further, Max. temperature of Earthwire exposed to sun: 530C |
|  | Number of Broken Wire Condition | Number of Broken wire for Suspension and angle towers are not mentioned in the specification. Kindly clarify number of wires broken condition. | - Following Broken wire conditions to be considered as per Tower Type: - 1) Suspension towers (DA) : Any one phase or ground wire/OPGW broken; whichever is more stringent for a particular member - 2) Small and medium angle towers (DB & DC): Any two phases broken on the same side and same span or any one phase and one ground wire/OPGW broken on the same side and same span whichever combination is more stringent for a particular member 3) Large angle tension towers/dead end towers (DD) : Any three phases broken on the same side and same span or any two of the phases and one ground wire/OPGW broken on the same side and same span; whichever combination constitutes the most stringent condition for a particular member |
|  | Wind For Broken Wire Condition | According to IEC 60826 and EN 50341-1 standard, Nil wind shall be considered for broken wire condition. Please confirm, if the same is in order. | For broken wire/ security condition, Following Loadings shall be considered:- - Further, as per clause 1.4.9 e), section IVA of Technical specification “Under broken wire condition, tower shall be designed considering transverse load based on maximum angle of deviation and longitudinal load based on minimum angle of deviation mentioned in Section-I of Technical specifications “ |
|  | Tower Design | As per section-IVA Tower design Clause. 1.4.9, Page 7 of 9, Design of towers shall be carried out by contractor as per IEC 60826 or EN-50341-1. We shall adopt IEC 60826-2017 and EN-50341-1:2012 standards for design of towers. Please confirm, if the same is in order. | The contractor shall design towers as per standards mentioned in Technical specification (latest revisions, with amendments/ changes adopted and published, unless specifically stated otherwise in the Specification). However, tower design shall also conform to design/ technical parameters mentioned in Technical specification/ clarification. |
|  | Scope of work, Section IA | We have noted from the scope of the Package TL01 & Package TL02 that both these Projects are same with change in conductor where package TL01 is triple bundle ACSR Condor Conductor and package TL02 is twin bundle ACSR Moose Conductor. We understand that the two packages are only two options with different conductor (type & arrangement) for same transmission line project. Hence we request you to merge the two packages and allow the bidders to quote for package TL01 as main and package TL02 as optional within the same tender. | Bidders to quote as per NIT. |
|  | Scope of work, Section IA | We understand that the complete design of transmission line towers and foundations are in the scope of contractor. Please confirm. | Bidder’s understanding is correct. |
|  | Scope of work, Section IA | We would like to request you to kindly share the route coordinate for the transmission line. | The Preliminary Survey report for 400kV D/C Lessos-Loosuk Transmission Project along with the KMZ file for coordinates for the terminal and Angle Points of line has been enclosed as Appendix-A-I & A-II, respectively. The Survey Report has been provided in good faith, and on best endeavour basis. Employer does not warranty, express or implied, or accept any responsibility or liability, whatsoever, in respect of any statements or omissions made in the Survey Report, or the accuracy, completeness or reliability of information contained therein, and shall incur no liability under any law, statute, rules or regulations as to the accuracy, reliability or completeness of such Survey Report, even if any loss or damage is caused to the Bidders by any act or omission on their part. Bidders shall make best efforts and carry out its own due diligence upon survey report provided by Employer and shall consider all possible techno-commercial factors before submission of Bid. Bidders may also visit the route of the Transmission Lines associated with the Project and the surrounding areas and obtain / verify all information which they deem fit and necessary for the preparation of their Bid. Bidders may also carry out required surveys and field investigation for submission of their Bid. |
|  | Nos. of Wire / Phase Broken | What will be the combinations of wire to be broken in broken wire condition , please clarify | Following Broken wire conditions to be considered as per Tower Type : 1) Suspension towers (DA) : Any one phase or ground wire/OPGW broken; whichever is more stringent for a particular member 2) Small and medium angle towers (DB & DC): Any two phases broken on the same side and same span or any one phase and one ground wire/OPGW broken on the same side and same span whichever combination is more stringent for a particular member 3) Large angle tension towers/dead end towers (DD) : Any three phases broken on the same side and same span or any two of the phases and one ground wire/OPGW broken on the same side and same span; whichever combination constitutes the most stringent condition for a particular member |
|  | Phase to Phase minimum Distance | What should be the Phase to Phase minimum Horizontal Distance , Please clarify | Refer Technical Specification SECTION-IV A (VOLUME-II), Clause 1.4.11 |
|  | L/r Value | What should be the L/r Values of all tower members, Please clarify | Please refer Technical Specification SECTION-IV A (VOLUME-II), Clause 1.4.9, wherein use of IEC 60826 & EN 50341-1 has been referred for Tower design. |
|  | Design Standards | Wind pressure and Loading calculation shall be as per IEC 60826 -- PLEASE CONFIRM | Please refer Technical Specification SECTION-IV A (VOLUME-II), Clause 1.4.9 for wind pressure & loading. |
|  |  | Member capacity calculation as per -EN 50341--- PLEASE CONFIRM | Please refer Technical Specification SECTION-IV A (VOLUME-II), Clause 1.4.9 |
|  | Electrical clearance Value | Live Metal clearance value as per clause 1.4.2. for 400 kV lines and altitude upto 3000 meters value furnished for no swing condition is different for suspension tower and tension tower (Jumper)--- please clarify | Bidders to consider Live Metal clearance values as per SECTION-IV A (VOLUME-II) clause 1.4.2 |
|  | Ground Clearance | As per Clause 2.3.1 on page 5 of 8 of SECTION-I A (VOLUME-II), Rev 0 (July’2022) it is understood that ground clearance of 8840 mm for altitude up to 1000 m is furnished and further increase due to higher altitude is left on bidder. Ground clearance is statutary requirement for any country, Hence, It is highly recommended to provide fixed values of Ground Clearance for altitude upto 1500 meter and for 1500 to 3000 meter. This will also keep all bidders at par in terms of technical requirements. | Please refer SECTION-I A (VOLUME-II) clause 2.3.1. |
|  | Loading Conditions | Loading conditions not found in tech spec, request to provide list of loading conditions along with relevant load criteria for each tower type design. | Please refer Sr. no. 1 , 3, 4 & 5, above. |