| Sr. No. | Clause No. and Details | Bidder's Query/Comment | Reply from POWERGRID |
| --- | --- | --- | --- |
|  | Route Alignment | As per response to Clarification 02, Sr. no 38, we understand that Route Alignment and Detailed Survey both have been carried out by Employer during bid stage itself and, the reports shall be given to successful bidder during execution. Employer has given the BOQ provision for Detailed Survey - 25 Km towards unforeseen changes. We understand that bidder needs to quote their prices for mentioned 25 Km Detailed survey works only. Kindly confirm if our understanding is correct. | Bidders understanding is correct. |
|  | Check Survey | We understand that Contractor has to carry out the profile works / Check survey works based on Reports of Route Alignment / Detailed Survey carried out by Client. Please confirm if our understanding is correct | - Bidders understanding is correct. |
|  | Indicative BOQ Service BOQ | As per Indicative BOQ, Sch Service BOQ – Item no 2 Detailed Soil Investigation: Quantity mentioned for Soil Investigation as per Soil type in Service BOQ is not clear and not in line with Technical specification. As per Technical specification, the requirement of Soil Investigation with SPT and DCPT is mentioned. Kindly provide the Correct BOQ for Soil Investigation in line with technical specification. | The Standard Penetration Test shall generally be used for detailed field investigation of soil strata whereas other methods may be used for Special locations only. The existing Service BoQ for Soil Investigation holds good. |
|  | Section details/ coordinates for Bird Divertors | Kindly provide the section coordinates/details wherein the Bird Divertor shall be envisaged | - Bird diverters shall be placed in identified stretches as per the conditions, if any, stipulated by forest authority or other appropriate authority, during execution of the project. |
|  | Section details/coordinates for Aircraft warning spheres | Kindly provide the section details wherein the Air craft Warning lights shall be envisaged | - Air craft Warning lights shall be placed in identified stretches as per the conditions/requirement, if any, stipulated by Kenyan Aviation Authority, during execution of the project. |
|  | LILO | Kindly confirm the LILO scope involved is only pertaining to OPGW works as mentioned in Service BOQ Item II – LILO Portion and not with main principal line with ACSR CONDOR conductor | - LILO work involves LILO of both circuit of existing 400kV D/C Loiyangalani-Suswa line at proposed 400kV Loosuk Substation with Triple Condor Conductor including OPGW. |
|  | Clarification 02 Sr. no .33 | As per response to clarification 02, Sr. no 33, it is mentioned to refer Amendment 02 for clarification on quantities to be considered for vibration dampers. However, in amendment 02, there is no mention of the same. Kindly clarify. | - Since Triple Spacer Damper for Conductor is envisaged in TL01 Package, there is no separate requirement for vibration dampers for conductors. |
|  | Cl.2.4.1, Section-1A, Technical Specification and Section-IV Indicative BOQ Quantities for Leg Extensions | In Cl. 2.4.1, Section-1A, Technical Specification, it is mentioned that for spans less than and greater than normal span, adequate clearance can be achieved by providing Leg / Body Extension (-ve or +ve) attached to Normal Tower or Basic Tower Body. But as per quantity given in the Indicative BOQ, there is no quantity mentioned for -ve Leg Extensions. Please clarify regarding this. | - Bidders has to quote as per BOQ/ BPS sheet. |
|  | Service BOQ in Indicative BOQ Quantity mentioned for Survey and Detailed Soil Investigation | In Service BOQ, SCHEDULE-1, Point No. 1, Km have been mentioned for Survey. But there is difference in Km for Detailed Survey and Check Survey. Similarly, in SCHEDULE-1, Point No. 2, Number of locations for detailed Soil Investigation have been mentioned. But the number of locations mentioned for Detailed Soil Investigation are not matching with the total quantity. Please clarify regarding above. | Detail Survey & Geotechnical Investigation is under progress by Survey Agency. Route alignment report has already been shared in bidding document. Provision of 25 kms detail survey has been envisaged for any unforeseen changes in the route at the time of construction of transmission line. Regarding number of locations mentioned for detailed soil investigation, Bidders has to quote as per BOQ/ BPS sheet. |
|  | Item no. 45, Clarification No. 2 | As per the clarification we have to refer to amendment issued for the technical specification of 160kN Insulator but we couldn’t find it under amendment. Please furnish the same. | For 220kV Line, insulator to be used should be 90kN & 160kN. The abstract of amendment in this regard is once again furnished below:- Sl. No.; Description; Unit; 220 kV AC (single CANARY). 90 KN; 160 KN. 1; Size and Designation of Ball & Socket assembly; mm; 16 mm (Alt-B); 20 mm. 2; Core diameter*; mm; 20; 20. 3; Nominal length; mm; 2320^; 2550^. 4; Minimum Creepage distance; mm; 7595; 7595. 5; No. of grading rings (min.); Nos.; 1; 1. 6; Nominal Outer Diameter of grading ring. a); Covered ring ***; mm; NA; NA. b); Other rings (Open type); mm; 200; 200. 7; Depth of grading ring (open type); mm; 105-125; 105-125. |
|  | 01_2 SECTION-I B GENERAL INFORMATION | As per Clause No 2.1 , The bidder/ Contractor should be a POWERGRID approved vendor of Tower and Tower Parts as on originally scheduled last date of bid submission or should have assured access from tower manufacturers approved by POWERGRID as on date of NOA. In case of assured access from tower manufacturers, the Contractor shall furnish a Joint Deed of Undertaking (Format enclosed at Annexure-A) along with the manufacturer(s) to guarantee quality & timely supply of tower parts and confirming to furnish a performance guarantee of 2% of the cost of such tower parts from each of the manufacturer(s) at the time of finalizing the manufacturer(s), during execution of the Contract. Please confirm if the this performance guarantee of 2% of the cost of such tower parts will be additional to the 10% performance guarantee mentioned under clause no 13.3.1 of PCC. | - This performance guarantee of 2% of the cost of such tower parts will be in addition to contract performance guarantee to be submitted by the Contractor on award of contract. |
|  | 01_2 SECTION-I B GENERAL INFORMATION | As per Clause No 2.1 (a) (i) OPGW manufacturer must have manufactured, type tested (as per IEC or equivalent standard) and supplied at least 100 km of OPGW during last seven (7) years and the same must be in satisfactory operation$ for at least one (01) year on 66kV or above transmission line(s), as on the date of NOA. OR (ii) OPGW manufacturer must have manufactured, type tested (as per IEC or equivalent standard) and supplied at least 100 km of OPGW as on the date of NOA. Further, extended warranty of one (1) year over and above the warranty period specified for OPGW shall be submitted. (b) OPGW manufacturer established as Subsidiary/ JVC/ Group company who has manufactured, type tested (as per IEC or equivalent standard) and supplied OPGW but not meets the requirement at (a)(i) above, shall also be considered, provided its Parent/ Principal company meets the requirement at (a)(i) above Further the following shall also be submitted by OPGW manufacturer (i) Performance guarantee for an amount of 3% of the cost of OPGW cable. (ii) Valid collaboration agreement (between Parent/ Principal and OPGW manufacturer) for technology transfer/ license to design, manufacture, test and supply OPGW in India. We understand that if the OPGW manufacturer meets the requirements mentioned in clause 2.1 (a) i or ii, then the above Performance Guarantee of 3% will not be required. Please confirm if our understanding is correct. | Bidders understanding is correct. |
|  | 01_2 SECTION-I B GENERAL INFORMATION | As per Clause No 2.13, The bidder/ Contractor should have its own manufacturing facilities & experience as stipulated below or should have assured access to supply the pole structures from Qualified Manufacturer(s) meeting individually the following minimum requirements and must demonstrate that based on known commitments they will be available for use in the proposed contract: - The qualified manufacturer should have its own manufacturing facilities for transmission line pole structures. Further, the qualified manufacturer should have designed, manufactured and either type tested or supplied transmission line pole structures for 66kV or above voltage transmission line. In case the Contractor is proposing supply of pole structures from his sub vendors( s), the Contractor will be required to furnish a performance guarantee of 2% of the cost of such transmission line pole structures from the manufacturer(s) at the time of finalizing the manufacturer(s), during execution of the (Format enclosed at Annexure-C) Please confirm, if the this performance guarantee of 2% of the cost of such transmission line pole structures will be additional to the 10% performance guarantee mentioned under clause no 13.3.1 of PCC. | This performance guarantee of 2% of the cost of such transmission line pole structures will be in addition to contract performance guarantee to be submitted by the Contractor on award of contract. |
|  | Cl 1.9, Section - IB, Volume II | As per Clause No 1.9, Access to the Line and Right of Way in Specification of Transmission Line (Section – General Information) The Contractor shall use existing road as much as possible. When streams or paths crossed by new access roads, necessary culverts of adequate size would be provided to avoid flooding of water. New access roads to be constructed by the Contractor shall avoid environmentally sensitive location. Special care should be paid to avoid disturbance to the wild animal’s migratory path. From above we understand that contractor has to construct motorable access road in the line corridor, which shall be 5 meters wide properly compacted & without any filling material. These roads shall be prepared only in those areas where existing roads are not available. All payments towards acquisition & compensation of land for access road route shall be in client’s scope. Please confirm if our understanding is correct. | Refer Technical Specifications, Section-I-B, General Information, Clause 1.9 regarding Access to the Line and Right of Way. Only Right of way and way leave clearance along the line route shall be arranged by the Employer. All other costs of providing and maintaining entry routes for line construction shall be borne by the Contractor. Contractor shall construct motorable access road of 5 meters width in the line corridor, which shall be properly compacted & without any filling material. Further, Bidders to quote as per TS and BPS-Service BoQ, Schedule-I, item sr. no. 3.0. |
|  | Cl 1.6, Section - IV C, Volume II | From the refered clause, we understand that the galvanization requirements applicable for projects TL01, TL02 are as below 1. For fabricated tower parts for thickness 5mm and above : 610 gm per sq.m 2. For fabricated tower parts for thickness 5mm and below : 460 gm per sq.m 3. For bolts and nuts : 460 gm per sq.m Please confirm our understanding. | As per Clause 1.6.1 of Technical Specifications Section-IV-C Tower: Materials, Fabrication, Erection & Stringing, “The fabricated tower parts and stubs shall have a minimum overall Zinc coating of 610 gm per sq. m of surface area except for plates & sections below 5mm which shall have Zinc coating of 460 gm per sq. m of surface area.” Regarding galvanization of Bolts & Nuts, refer Clause 1.6.2 of Section-IV-C of TS. |
|  | PCC 39.4 (TL01, TL02, SS01, SS02, SS03) | As per PCC 39.4, we understand that the quantities given in the price schedule are preliminary & tentative. Payment to the contractor shall be made based on actual executed quantities which shall be arrived after detail survey and soil investigation during execution. Please confirm if our understanding is correct. | Bidders understanding is correct. |
|  | Inspection, Testing & Inspection Certificates (Section II, General Technical Conditions, Clause no. 1.8.1.5) | As per Section II, General Technical Conditions, Clause no. 1.8.1.5, Page no. 10 of 22, It is mentioned that “The Employer reserves the right to witness any or all type, acceptance and routine tests specified for which the Contractor shall give the Employer/ Inspector Twentyone (21) days written notice of any material being ready for testing for each stage of testing as identified in the approved quality plan as customer inspection point (CIP) for indigenous inspections. All inspection calls for overseas material shall be given at least forty-five (45) days in advance. Such tests shall be to the Contractor’s account except for the expenses of the Inspection Engineer”. We understand that, the bidders are not required to consider the air fare, visa charges, local travelling allowance, hotel stay, per diem allowance or any other charges for the Employer’s Inspection Engineers with regards to witness/type tests/routine test. Kindly confirm our understanding is correct. | Bidders understanding is correct. |
|  | The minimum drop point of grease (Conductor) | In technical specifications, the grease application case is mentioned but the minimum drop point of grease is not mentioned. Kindly confirm the minimum drop point of grease. | Refer Clause 1.1 of TECHNICAL SPECIFICATIONS, SECTION-VIIA, CONDUCTOR wherein IEC 61394/ EN 50326 has been specified for grease. It is clarified that Type-A grease as per above Standards shall be provided. |
|  | Reliability Level for Triple ACSR Condor Conductor | What is the reliability level to be considered for Triple ACSR Condor conductor? | Reliability level for Tower design with Triple conductor shall be 1. Refer Section IVA of Technical specification |
|  | Section-III, Evaluation and Qualification Criteria, Part-1 of Bidding Documents | PQR Amendment Request as:. 1.3 Joint Venture Bids: a. ii) The lead partner of Joint Venture shall meet the Technical Experience criteria given at Para 1.1(b) and not less than 50% of the Technical Experience criteria given at Para 1.1 (a) & (c) above and not less than 40% of the Financial Position criteria given at Para 1.2 (b) & (c) above.. | Provisions of bidding documents remain unchanged |