| Sr. No. | Clause No. and Details | Bidder's Query/Comment | Reply from POWERGRID |
| --- | --- | --- | --- |
|  | Employer’s Responsibilities - Right of Way | As per Section VIII – General Conditions of Contract, Clause 10.2, It is mentioned that “The Employer shall be responsible for acquiring and providing legal and physical possession of the Site and access thereto, and for providing possession of and access to all other areas reasonably required for the proper execution of the Contract, including all requisite rights of way”. We understand that, all the right of way, way leave clearance and access road will be in the scope of Employer. Kindly confirm if our understanding is correct. | Refer Technical Specifications, Section-I-B, General Information, Clause 1.9 regarding Access to the Line and Right of Way. Only Right of way and way leave clearance along the line route shall be arranged by the Employer. All other costs of providing and maintaining entry routes for line construction shall be borne by the Contractor. The provision of TS prevails over GCC. Bidders to quote as per TS and BPS-Service BoQ, Schedule-I, item sr. no. 3.0. |
|  | Employer’s Responsibilities - Right of Way Compensation | As per Section VIII – General Conditions of Contract, Clause 10.3, It is mentioned that “The Employer shall acquire and pay for all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the country where the Site is located”. We understand that, all the right of way compensation to the landowners will be in the scope of Employer. Kindly confirm if our understanding is correct. | Refer Technical Specifications, Section-I-B, General Information, Clause 1.9 regarding Access to the Line and Right of Way. Only Right of way and way leave clearance along the line route shall be arranged by the Employer. All other costs of providing and maintaining entry routes for line construction shall be borne by the Contractor. The provision of TS prevails over GCC. |
|  | Outline Diagrams of Towers | Outline diagram of 400kV D/C towers are not furnished with the tender specification. We request you to kindly furnish 400kV D/C suspension & tension tower outline diagrams. | Outline diagram/SLD is to be prepared based on parameters mentioned in TS & Tower design which is in the scope of contractor. |
|  | Altitude Range | As per Volume II, Section-IV A – Tower Design, Clause no. 1.4.2 –Live Metal Clearance (For 400kV Transmission Lines), Page no. 4 of 9, Altitude upto 1500m and altitude from 1500m to 3000m are specified. We will consider 1500m altitude & 2250m altitude respectively for tower design calculations. Kindly confirm | Tower shall be designed considering maximum altitude mentioned in the respective tower package. |
|  | Slenderness Ratio Limitation | We request you to kindly furnish slenderness ratio limitation for Leg, Lattice, Belts, Bracing & redundant members. OR Kindly confirm, if it is to be followed as per BSEN-50341, 2012. | Please refer Technical Specification SECTION-IV A (VOLUME-II), Clause 1.4.9, wherein use of IEC 60826 & EN 50341-1 has been referred for Tower design. |
|  | Basic Wind Velocity | As per Technical Specification, Section-IA, (Standard) scope of work, Clause 4 – Service Conditions, It is mentioned that “Basic wind velocity is mentioned as 46m/s”. We presume that it is design basic reference wind speed of 46m/s as mean value of wind during 3s gust at a level of 10m above ground. The design reference wind speed of 46m/s will be converted to 10min period at a level of 10m above the ground for tower designs. Please confirm the same is in order. | Basic wind speed to be considered for calculating wind pressure is 46 m/sec for 03 sec gust. This wind shall be converted to 10 min. mean value. Other factors viz. terrain category, Gust, etc. shall also be considered for calculating design wind pressure. |
|  | Foundation Design | As per Section-IVD, Foundation Design, Clause 1.6.2 – Design Criteria, It is mentioned that “The overload factors for open type foundation shall be 1.1” and As per Clause 1.6.1 – Design Criteria, It is mentioned that “Partial safety factor shall be 1.5 for concrete and 1.15 for steel”. We shall not apply any partial safety factor for soil properties mentioned on Table 1 – Soil Properties on page 8 of 18. The foundation shall be designed accordingly. Please confirm the same is in order. | Standard foundation shall be designed by the contractor based on soil parameters mentioned on Table 1 – Soil Properties. - Partial Safety factor for soil properties mentioned on Table 1 need not to be applied. |
|  | Tower Design | As per Technical Specification, Section-IVA – Tower Design, Clause 1.4.9 – Tower Loading Conditions (Note - i), “The final unloaded tension of conductor at everyday temperature shall not exceed 22 percent of the ultimate tensile strength of conductors”. Whereas, As per Section-IVA – Tower Design, Clause 1.4.9 – Tower Loading Conditions (Note - ii), in same section clause it is stated that “For normal towers, the value of final unloaded tension of conductor at everyday temperature considered for Tower Design under Safety Condition and Anti-cascading condition shall not be less than 25% of the ultimate tensile strength of conductors for below 400kV voltage level transmission lines”. As per above notes, for everyday temperature both the conditions cannot be satisfied at the same time. We will follow (Note - i) for tension limitation on conductor. Kindly confirm | The provision mentioned in Clause 1.4.9 (Note - i) is for tension limitation on conductor and (Note - ii) is related to design of tower. |
|  | Conductor (Greased or Ungreased) | As per Technical Specification, Section VII-A – Conductor, Clause 1.1.1, It is mentioned that “To avoid the risk of corrosion, a uniform layer of anticorrosive grease shall be applied to the conductor as per Case-2 of IEC 61089, Annexure-C. The applied grease shall fulfil the testing requirements as stipulated in the IEC 61394/EN 50326”. As per Supply BOQ, A.1 – SCHEDULE-I, SL.NO. 7 (i), the contractor has to supply the ACSR Condor Conductor for this project. We request you to confirm, if the conductor to be supplied for this project should be greased or ungreased. | The conductor to be supplied for this project should be greased. |
|  | Section-IV Indicative BOQ | For TL01 & TL02, in Section IV, Indicative BOQ (Supply BOQ & Service BOQ) is given. Quantities and all items are matching in both packages TL01& TL02. Same Line name has been shown in both both packages. But for TL01 Line with ACSR Triple Condor Conductor has shown and for TL02, Line with ACSR Twin Moose Conductor is shown. This is not exactly clear. We understand prices are required for both i. e. Line with ACSR Triple Conductor and ACSR Twin Moose Conductor. Please confirm our understanding is correct. | Bidders understanding is correct. |
|  | Technical Specification | We have checked. In Technical Specification, Co-ordinates for End Points of Line and Angle Points are not given. Please furnish the same for checking the route | Coordinates for route already available in Bid document. Refer Bid Document: Amendment No-I and Clarification No-I dated 02-Aug-2022. |
|  | Cl. 2.3.1, Section -1A, Technical Specifications | In Cl. 2.3.1, Section-1A, Technical Specification, Ground Clearance value is mentioned as 8840 mm is specified for altitude upto 1000m. But nothing has been specified for altitudes more than 1000m. And as per BOQ and Technical Specification, Altitude required is upto 3000M. Hence we request you to furnish the value for Ground Clearance for Altitude more than 1000M. | a) Minimum Ground Clearance value for 400kV level line (For altitude up to 1500m ) : 9.1 m b) Minimum Ground Clearance value for 400kV level line (For altitude from 1500m to 3000m): 9.8 m c) Minimum Ground Clearance value for 220kV Line (For altitude upto 2000m): 7.3 m |
|  | Cl. 4, Section -1A, Technical Specifications | In Cl. 4, Section-1A, Technical Specification, Climatic Conditions are given. In this, Basic Wind Velocity is given as 46 m/s. But it is not mentioned that whether is 10min or 3s Gust velocity. In this regard, we understand that the value 46m/s given is to be considered as Reference Wind Speed (VR) @ 3s Gust and at a level 10m height above Ground Level. And Wind Pressure on Conductor, Earthwire and Tower is to be calculated as per IEC 60826. Please confirm our understanding is correct. | Basic wind speed to be considered for calculating wind pressure is 46 m/sec for 03 sec gust. This wind shall be converted to 10 min. mean value. Other factors viz. terrain category, Gust, etc. shall also be considered for calculating design wind pressure. |
|  | Cl.1.4.9, Section IVA, Technical Specification | In Cl. 1.4.9, Section IVA, Technical Specification, it is mentioned that design of Tower will be done as per 1. IEC 60826 - Design Criteria of overhed Transmission Lines. 2. EN-50341-1 - Overhead Electrical Lines exceeding AC 1 KV Part-1:General Requirements - Common Specification. It is not exactly which standard is to be referred. In this regard, we understand as below. 1. Loading are to be calculated as per IEC60826. 2. Loading Cases are to be condiered as per IEC 60826 as no Loading cases are mentioned. 3. Design for members is to be done as per ASCE 10-15 SEI standards. Please confirm our understanding is correct. | Loading Condition & weather condition as per Technical specification, IEC 60826 (latest revision) & Clarification issued. Member design of Tower as per BSEN- 50431-1:2012 (Latest). |
|  | Cl.1.4.9, Section IVA, Technical Specification | In Cl. 1.4.9, Section IVA, Technical Specification, Tension Limit for EDS (Everyday Temperature @ Nil Wind) has been specified for Conductor and Groundwire. But nothing has been mentioned about the temperature and tension limits required for Full Wind Condition (Maximum Tension). Please furnish the same. | Please refer Amendment-2. Maximum tension limit under everyday temperature full wind condition shall not exceed 70% of UTS of Conductor. |
|  | Section-IVA, Tower Design, Technical Specification | In Seection-IVA, Tower Design, nothing has been specified mentioned about member thickness to be considered for design members. In absence of Data we are considering Member Thickness for Design Members as below :- 1. Leg Members, Lower Member for Cross Arms and Peak Member = 5mm. 2. Secondary Members carrying stress = 4 mm. 3. Redundant Members = 4 mm. 4. Gusset Members = 4mm. Kindly confirm. | Refer Amendment-2 for minimum thickness of member. The thickness of the gusset plate, required to transmit stress, shall not be less than that of the thinnest of connected member but not less than 5 mm in any case. Minimum thickness of gusset shall be 2 mm more than lattice it connects only in case when the lattice is directly connected on the gusset outside the leg member. Minimum thickness of galvanized tower members shall be as follows: i) Leg members, groundwire, peak member and lower members of cross arms in compression: 5 mm ii) Other members: 4 mm |
|  | Cl.1.4.9, Section IVA, Technical Specification | In Cl. 1.4.9, Section IVA, Technical Specification, it is mentioned that design of Tower will be done as per 1. IEC 60826 - Design Criteria of overhed Transmission Lines. 2. EN-50341-1 - Overhead Electrical Lines exceeding AC 1 KV Part-1:General Requirements - Common Specification. It is not exactly which standard is to be referred. In this regard, we will calculate Loadings as per IEC60826. Nothing has been metioned about Partial Safety to be considered for Tower Loading and Design. We understand Loads calulated as per IEC 60826 are ultimate and no additional factor is to be considred. Please confirm our understanding is correct. | Tower Design shall be carried out as per Technical specification, IEC 60826 (latest revision) & EN-50341-1 (latest revision). |
|  | - | As per Clarification for (400kv) point no 4 & (220 kV) point no 1, It is clarified to consider basic design reference wind speed of 46 m/s for 10 min period at height of 10m above ground.. We feel that this wind speed of 46m/s should be 3 s gust wind speed & mean wind speed for 10min period & 10m height should be around 33.5m/s. (Clarification for the same is already asked by us for which reply is awaited). If we consider basic wind speed @ 10m ht for 10min period as 46m/s instead of 33.5m/s, then the tower loadings will be almost double resulting in very heavy towers & fdns.. Also we have not encountered such high value of wind speed in earlier project/ tenders in Kenya.. | Basic wind speed to be considered for calculating wind pressure is 46 m/sec for 03 sec gust. This wind shall be converted to 10 min. mean value. Other factors viz. terrain category, Gust, etc. shall also be considered for calculating design wind pressure. |
|  | Bill of Quantity Supply BOQ - TL01 | We understand that material required for LILO of Loyangalani-Suswa 400kV D/C Line at Loosuk Substation (with ACSR Triple Condor) is included in the total quantities mentioned in the BOQ. Please confirm. | The quantities pertaining to LILO of Loyangalani-Suswa 400kV D/C Line at Loosuk Substation (with ACSR Triple Condor) is included in BoQ. |
|  | Bill of Quantity Supply BOQ - TL01 & TL02 Item No. 7 (i) & (ii) | We understand that quantity includes extra length towards Sag/Wastages. Please advise the extra length over and above and the horizontal length which will be considered towards Sag/wastages. | Refer Clause 3.13 regarding Permitted Extra Consumption of Line materials of TECHNICAL SPECIFICATIONS SECTION- IV C, TOWER: MATERIALS, FABRICATION, ERECTION & STRINGING |
|  | General | Please provide the List of approved vendor/Manufacturer, if any. | List of approved vendor/Manufacturer available in POWERGRID wesite following Link: https://apps.powergrid.in/ims/50-0001-002.aspx. Further any new vendor proposed by Contractor may also be considered for approval, as per Annexure-I of TS, SECTION-II, GENERAL TECHNICAL CONDITIONS |
|  | Wind -Angle of Incidence | We assume that the angle of incidence of wind is 0 deg only for which the Tower has to be designed. Please confirm. | Angle of incidence of wind to be considered for Tower Design shall be 0 deg, 30 deg, 45 deg. |
|  | Design Code | The Tower shall be designed based on ASCE10-15. Please confirm | Please refer Technical Specification SECTION-IV A (VOLUME-II), Clause 1.4.9, wherein use of IEC 60826 & EN 50341-1 has been referred for Tower design. Further, also refer Refer Technical Specifications, Section-II, General Technical Conditions, Clause 1.2 regarding Compliance with Standards |
|  | Load Factor | Load Factor for the Tower Design are not provided, We undersatnd that the load factors to be considered as per EN50341. Please Confirm. | Strength Factor for steel material in tower design shall be considered as 0.98. Further refer amendment in TS in this regard. |
|  | Foundation forces For design | We consider that the foundtaion shall be designed based on the ultimate forces derived from the Tower Design and other load factors are required. Please confirm | For Foundation loadings, ultimate reactions from tower shall be multiplied by load factor. Load factor shall be referred from Clause 1.6.2 of TECHNICAL SPECIFICATIONS SECTION-IV D, CONTRACTOR DESIGN FOUNDATIONS. |
|  | Member Thickness | Minimum Thickness of Member has not been provided. we are considering 3mm as minimum thickness for all the members. Please confirm. | Refer Amendment-2 for minimum thickness of angle member. |
|  | Ground Clearance | As per Section 1a, The ground clearance provided is for 1000m Altitude. We assume that the Tower has to be deisgned considering the clearance provided for only 1000m Altitude. Additional ground clearance if required can be achived through Extensions. Please confirm that our assumption is correct. | For TL01 & TL 02 package, Tower Geometry shall be finalized based on electrical and Ground clearance, Length of Insulator, etc. for (a) 1500m altitude (b) 3000m altitude. |
|  | Ground Clearance | In order to avoid confusion and to standardize the Tower geometry, we kindly request you to porivde one standard ground clearance value which shall be adopted through out the line (which included of all altiude correction factors). | a) Minimum Ground Clearance value for 400kV level line (For altitude up to 1500m ) : 9.1 m b) Minimum Ground Clearance value for 400kV level line (For altitude from 1500m to 3000m): 9.8 m c) Minimum Ground Clearance value for 220kV Line (For altitude upto 2000m): 7.3 m |
|  | Wind for Broken Wire Condition | For Broken wire/Security condition the loading conditions for wind are mentioned in the referred clarification Temperatures to be considered for the conditions highlighted in clarification no.1 point no 7 are missing in the table. Hence, We are considering every day temperature (EDT) for the loading conditions given in clarification no.1 point no.7 Please confirm our considerations. | Bidder's understanding is correct. |
|  | Loading Condition for Construction & Maintenance | For construction safety and maintenance condition, Every day temperature with nil wind condition shall be considered for calculation of cable loads and wind on tower. Please confirm our understanding. | Bidder's understanding is correct. |
|  | Loading Condition for Reliability Normal | For reliability normal condition, Everyday temperature with full wind condition shall be considered for calculation of cable loads and wind on tower. Please confirm our understanding. | Bidder's understanding is correct. |
|  | Design - Basic Wind Velocity | With reference to respective bidder's query,PGCIL confirmed that Basic Wind velocity 46m/s provided in technical specification is mean value of wind during 10 min period at a level of 10m above ground. At actual, provided wind velocity of 46m/s should correspond to 3 seconds gust at 10.0m height. We request re-confirm on this point as 3 sec gust wind speed at 10.0m height, or else if we proceed as per clarification no-1 point no.4, calculated wind on structures and cables will be abnormally high resulting uneconomical design and commercial proposals. | Basic wind speed to be considered for calculating wind pressure is 46 m/sec for 03 sec gust. This wind shall be converted to 10 min. mean value. Other factors viz. terrain category, Gust, etc. shall also be considered for calculating design wind pressure. |
|  | Supply BoQ- SCHEDULE 1, Item no 10.0, Conductor Accessories for triple bundled "Condor" Conductor -TL01 & Supply BoQ- SCHEDULE 1, Item no 10.0, Conductor Accessories for twin bundled "Moose" Conductor -TL02 | As per the referred item no 10.0, we understand that vibration dampers are not provided in the accessories list for both the TL01 & TL02 packages. We request for indicative quantities for vibration dampers in both the packages and provide us the amended price schedules. | Please refer Amendment for revised BoQ for TL 02 Package. |
|  | Part-1, 06-Section-IV, Indicative BOQ_Package TL 01 & TL 02 | We understand that all the TL packages in SS03/TL01/TL02 are item rate and re-measurable contracts. Payments will be made for actual executable quantities during execution phase. Please confirm our understanding. | Bidder's understanding is correct. |
|  | Part-1, 06-Section-IV, Indicative BOQ_Package TL 01 & TL 02 | We understand that, bidders are not supposed to change the quantities provided in Indicative BOQ's of all packages. Please confirm our understanding. | Bidder's understanding is correct. |
|  | Ground Clearance Requirements for Different altitudes | We request PGCIL to declare the ground clearance requirements at all required altitude levels of the TL packages which makes all the bidders to consider the same in their designs. As per clarification response point no 17, the same was left to bidder which results in different outcomes and may result in either inadequate or very high clearance requirements. Hence, we request for fixed ground clearance values at different altitudes. | a) Minimum Ground Clearance value for 400kV level line (For altitude up to 1500m ) : 9.1 m b) Minimum Ground Clearance value for 400kV level line (For altitude from 1500m to 3000m): 9.8 m c) Minimum Ground Clearance value for 220kV Line (For altitude upto 2000m): 7.3 m |
|  | Type Test Requirements of Towers | We request to add a separate line item of Tower Testing requirements of each package separately in services BOQ Service Schedule, enabling all the bidders to consider the same number of towers to be type tested in their proposals. | As per Clause 1.3.5.2 of TECHNICAL SPECIFICATIONS, SECTION-IV B, TOWER TESTING, Type test charges for tower testing are deemed to be included in fabrication charges quoted by bidder. Bidder to quote fabrication charges accordingly. |
|  | Boq Service Schedule, Detail & Check Survey quantity | We observed that the detail survey quantity is 25km and check survey quantity is 180km for the packages TL 01 & 02. We presume that complete detail survey and check survey are in scope of bidder and both the quantities shall be same. If in case, detail survey is already completed by the client, we request to provide detail survey inputs which enables all the bidders to consider the terrain features while submitting their proposals. | Detail Survey is under progress by Survey Agency. Route alignemnt report has already been shared in bidding document. Provision of 25 kms detail survey has been envisaged for any unforeseen chages in the route at the time of construction of transmission line. |
|  | Clause 2.3.1 of TS Volume-II, Part-2A, Section – 1A | As per Clause 13.3.1 of IS:5613 (Part2/Sec1), live metal clearances above 1000 m altitude shall be increased by 1.25% for every 100m height or part thereof but however it is not specifically mentioned for ground clearance. In absence of formula for ground clearance, we have calculated the ground clearance using the above formula, {8.84 + (8.84*0.0125*5)} = 9.4 m for 1500 m altitude and {8.84 + (8.84*0.0125*20)} = 11.05 m for 3000m altitude. Kindly confirm the same else provide the required formula for calculation of ground clearance as per required altitude. | a) Minimum Ground Clearance value for 400kV level line (For altitude up to 1500m ) : 9.1 m b) Minimum Ground Clearance value for 400kV level line (For altitude from 1500m to 3000m): 9.8 m c) Minimum Ground Clearance value for 220kV Line (For altitude upto 2000m): 7.3 m |
|  | Clause 1.4.9 (a) of TS Volume-II, Part-2A, Section – IVA | As IEC and IS codes for tower design criteria/methodology are akin, kindly confirm the use of IS code for design. | Refer Technical Specifications, Section-II, General Technical Conditions, Clause 1.2 regarding Compliance with Standards |
|  | Minimum Thickness & Minimum section Size for design member. | Kindly confirm the use of Minimum Thickness of 5mm for Legs & Main cross arm members and 4mm for other members with Minimum section Size of 45x30x4 in design of towers. Else please provide the thickness & minimum size of member to be used in design. | Refer Amendment for minimum thickness of angle member. Minimum thickness of galvanized tower members shall be as follows: i)Leg members, groundwire, peak member and lower members of cross arms in compression: 5 mm ii)Other members: 4 mm |
|  | Tower Load Test, Section IVB | We understand that all the tower type that will designed by the contractor shall be subject to type test as per the provision of tower load test, section IVB. Please confirm. | Bidders understanding is correct. |
|  | Rod Type Earthing, Indicative BOQ | Please provide technical specification, erection details and drawing for Rod type earthing requirement. | Refer Technical Specifications, Section-IV C, Tower: Materials, Fabrication, Erection & Stringing, Clause 1.7.9 and Section-XI: Tender Drawing (Drawing no. STD/RD/EARTH/001 ) for Rod Type Earthing |
|  | Aviation Markers | Please provide technical specifications for Aviation Markers & Bird diverters. | Span Marker: Coloured globules of 40-50 cm diameter made of reinforced fibre glass or any other suitable material, weighing not more than 4.5 kg each with suitable clamping arrangement and drainage holes shall be installed on the earth wire(s) in such a manner that the top of the marker is not below the level of the earth wire. Half orange and half white coloured globule should be used. Further, the guidelines, if any, issued by Kenyan Aviation Authority regarding span markers shall also prevails. For Bird Flight Diverter, refer Technical Specifications, Section-IV C, Tower: Materials, Fabrication, Erection & Stringing, Clause 1.3.7 |
|  | Section VIII, Composite Longrod Insulators | As per the indicative BOQ the requirement for 220kv is 220kv90kn and 220kv-160kn but as per specification Annexure-B the details are provided for 220kv-90kn and 220kv-120kn only. The required 160kn details are not provided. Request you to please provide the details for the same. | For 220kV Line, insulator to be used should be 90kN & 160kN. Further Refer Amendment in this regard. |
|  | PCC Clause 13.3.1 | Additional performance guarantee of 2% has to be provided by the contractor after DLP and should be valid for maintenance period. Is the maintenance period applicable for the project? if yes, what is the duration of maintenance period? | As per Technical Specifications Section- I-A under SCOPE, Maintenance of the line until completion of the defect liability period, is in Bidder’s scope. |
|  | Nos. of Wire / Phase Broken | What will be the combinations of wire to be broken in broken wire condition , please clarify | Following Broken wire conditions to be considered as per Tower Type : 1) Suspension towers (DA) : Any one phase or ground wire/OPGW broken; whichever is more stringent for a particular member 2) Small and medium angle towers (DB & DC): Any two phases broken on the same side and same span or any one phase and one ground wire/OPGW broken on the same side and same span whichever combination is more stringent for a particular member 3) Large angle tension towers/dead end towers (DD) : Any three phases broken on the same side and same span or any two of the phases and one ground wire/OPGW broken on the same side and same span; whichever combination constitutes the most stringent condition for a particular member. |
|  | Phase to Phase minimum Distance | What should be the Phase to Phase minimum Horizontal Distance , Please clarify | Refer Technical Specification SECTION-IV A (VOLUME-II), Clause 1.4.11 |
|  | L/r Value | What should be the L/r Values of all tower members, Please clarify | Please refer Technical Specification SECTION-IV A (VOLUME-II), Clause 1.4.9, wherein use of IEC 60826 & EN 50341-1 has been referred for Tower design. |
|  | Design Standards | Wind pressure and Loading calculation shall be as per IEC 60826 -- PLEASE CONFIRM | Please refer Technical Specification SECTION-IV A (VOLUME-II), Clause 1.4.9 for wind pressure & loading. |
|  |  | Member capacity calculation as per -EN 50341--- PLEASE CONFIRM | Please refer Technical Specification SECTION-IV A (VOLUME-II), Clause 1.4.9 |
|  | Electrical clearance Value | Live Metal clearance value as per clause 1.4.2. for 400 kV lines and altitude upto 3000 meters value furnished for no swing condition is differenct for suspension tower and tension tower (Jumper)--- please clarify | Bidders to consider Live Metal clearance values as per SECTION-IV A (VOLUME-II) clause 1.4.2 |
|  | Ground Clearance | As per Clause 2.3.1 on page 5 of 8 of SECTION-I A (VOLUME-II), Rev 0 (July’2022) it is uderstood that ground clearance of 8840 mm for altitude up to 1000 m is furnished and further increase due to higher altitude is left on bidder. Ground cearance is statutary requirement for any country, Hence, It is highly recommended to provide fixed values of Ground Clearance for altitude upto 1500 meter and for 1500 to 3000 meter. This will also keep all bidders at par in terms of technical requirements. | Please refer SECTION-I A (VOLUME-II) clause 2.3.1. |
|  | Loading Conditions | Descriptions of Loading conditions not found in tech spec , request to provide list of loading conditions along with relevant load criteria for each tower type design. | Please refer replies give above. |
|  | Sag tension consideration | To carry out sag tension calculation dynamic wind pressure on wires to be considered as per IEC 60826:2017 clause no 6.2.9----- please confirm. | Bidders understanding is correct. |
|  | Sag tension Condition | Provide all weather conditions need to consider during sqag tension calculation. | Sag tension calculation shall for Minimum ambient temperature, everyday temperature and maximum temperature of earthwire and conductor. |
|  | Loading Calculation | During loading calculation , wind on wire to be considered including relevant gust factor,drag coefficient etc. And mechanical tensions corresponding to dynamic wind pressure to be considered.-- Please confirm. | Wind Pressure on wire is to be calculated as per IEC 60826:2017 clause no 6.2.9 and mechanical tensions corresponding to dynamic wind pressure shall be considered. |
|  | Minimum thickness of member | Pease confirm minimum thickness of angle member can be used. | Refer Amendment for minimum thickness of angle member. |
|  | Use of Unequal angle sections | Pease confirm whether unequal angle member section can be used or not. | Only equal angle member section shall be adopted except 45x30x4 mm. |
|  | 1.2, iii Part-2A 01_1 Section IA (standard)ScopeRev-Package-TL01, Rev-0 | Kindly arrange to clarify the scope of Employer for RoW & Access road clearnaces along-with forest clearance, statutory payments etc. similar to the practices in Indian Projects | Refer Technical Specifications, Section-I-B, General Information, Clause 1.9 regarding Access to the Line and Right of Way. Only Right of way and way leave clearance along the line route shall be arranged by the Employer. All other costs of providing and maintaining entry routes for line construction shall be borne by the Contractor. The forest clearance and Statuatory payments shall be in the scope of Employer. However, proposal pertaining to all Statuatory clearance is to be prepared by Contractor. |
|  | 1.2, xx Part-2A 01_1 Section IA (standard)ScopeRev-Package-TL01, Rev-0 | Kindly arrange to clarify whether this scope could be excluded from the Bidder's scope of supply? | No, Bidder has to supply ERS as per BPS. |
|  | 1.2, xxii Part-2A 01_1 Section IA (standard)ScopeRev-Package-TL01, Rev-0 | Kindly arrange to clarify whether this scope could be excluded from the Bidder's scope of work? | No, Bidder has to quote as per scope of work mentioned in TS Section-IA. |
|  | Clause, 1.4.11 & Clarification reply to S.No. 13 | Refer to Clause, 1.4.11 Minimum Vertical Separation shall be 8m need to maintain; However, Horizontal phase to phase distance minimum requirement is not found. Therefore, request to provide the Minimum Horizontal Phase to Phase distance to be maintain. | The required horizontal phase to phase spacing shall be governed by the tower design for 400kV voltage level. |
|  | Clarification-1, S No. 14 | Refer to Clarification-1, S No. 14; L/r check shall be done based on IEC / BSEN code; However, please confirm whether it is required to design the Members & limits of L/r values as per BSEN 50431-1:2012. since L/r values & member capacity equations are not found in IEC 60826:2017. | Please refer Technical Specification SECTION-IV A (VOLUME-II), Clause 1.4.9, wherein use of IEC 60826 & EN 50341-1 has been referred for Tower design. |
|  | Clarification-1, S No. 8, 15 & 16 | Refer to reply to S. No. 8, 15 & 16 of clarification-1, It is not clear which code need to refer for Wind pressure calculation; Loading calculation & Member design of Tower. However request to please confirm the requirement of codes for each criteria. Otherwise, Please confirm below understanding is correct ◦ Wind Pressure calculation as per IEC 60826 (latest revision). ◦ Dynamic Wind pressure need to consider for Sag tension calculation for Conductor; Earthwire & OPGW; Span Factor / Gust factor will be applied during Load calculation on wire. ◦ Loading Condition & weather condition as per Technical specification & Clarification which are in line with IS-802 requirement. ◦ Member design of Tower as per BSEN- 50431-1:2012 (Latest). | Bidders understanding is correct. |
|  | Clause 2.3.1 of TS & reply to Clarification-1 S No.18 | As per Clause 2.3.1 on page 5 of 8 of SECTION-I A (VOLUME-II), Rev 0 (July’2022) & reply to S No. 18 in Clarification-1; as we have not found any reference to consider the Minimum Ground clearance for higher altitude, However request to provide the Minimum Ground Clearance value separately for altitude up to 1500m & for 1500m to 3000m. | a) Minimum Ground Clearance value for 400kV level line (For altitude up to 1500m ) : 9.1 m b) Minimum Ground Clearance value for 400kV level line (For altitude from 1500m to 3000m): 9.8 m c) Minimum Ground Clearance value for 220kV Line (For altitude upto 2000m): 7.3 m |
|  | Clause 1.4.2 of TS & Clarification-1 reply S No. 17 | As per clause 1.4.2. & Clarification-1 reply S No. 17; Live Metal clearance value for 400 kV lines and altitude up to 3000 meters value furnished for no swing condition is different for suspension tower and tension tower (Jumper). Generally without any swing live metal clearance requirement will remain same; However request to please reconfirm. | Provision of Technical Specification holds good. |
|  | Clarification-1, reply to S No.7 | As per Clarification-1, reply to S No.7; Only broken wire condition details provided which is as per IS code; However please confirm whether we have to consider other conditions viz, Reliability, Safety, Anticascading, Dead End conditions as per Indian Standand (IS-802) only. | Loading condition shall be referred from Technical Specification, IEC 60826 & EN 50341-1. |
|  | General | Please confirm minimum thickness of angle member can be used. | Refer Amendment for minimum thickness of angle member. |
|  | General | Please confirm whether unequal angle member section can be used or not. | Only equal angle member section shall be adopted except 45x30x4 mm. |
|  | Temperature Zone | As per technical specification for 400kV line (TL01), maximum altitudes specified as 1500m. However, minimum temperature of climate for this line specified is zone 3 as 5.0 Degree Centigrade. This 400kV line may pass through Snow Zone due to higher altitude. Hence kindly re-confirm the temperature of climate for the said 400kV line. | Line does not pass through snow zone. The temperature mention in TS is to be followed. |
|  | Minimum drop point of grease | As per Technical Specification, Section VII-A – Conductor, Clause 1.1.1, It is mentioned that “To avoid the risk of corrosion, a uniform layer of anticorrosive grease shall be applied to the conductor as per Case-2 of IEC 61089, Annexure-C. The applied grease shall fulfil the testing requirements as stipulated in the IEC 61394/EN 50326”. As per Supply BOQ, A.1 – SCHEDULE-I, SL.NO. 7 (i), the contractor has to supply the ACSR Condor Conductor for this project. We understand that, Case-2 of IEC 61089 greasing shall be applied on ACSR Condor Conductor. However, the minimum drop point of grease is not mentioned. We request you to please provide the minimum drop point of the grease which shall be applied on ACSR Condor conductor. | Refer Clause 1.1 of TECHNICAL SPECIFICATIONS, SECTION-VIIA, CONDUCTOR wherein IEC 61394/EN 50326 has been specified for grease. It is clarified that Type A grease as per above Standards shall be provided. |
|  | Tower Painting | As per Technical Specification, Section I-A, Scope, Clause no. 1.2 (xvi), It is mentioned that “Painting of towers & supply and erection of span markers, obstruction lights (wherever applicable) for aviation requirements (as required)”. We understand that, there is no scope for tower painting in the said proposed tender. Kindly confirm | For Tower Painting, Refer Service BoQ, Item no.16.3. |
|  | 07_1 Section VII A Conductor,Rev-0(July'2022) | Kindly confirm the minimum drop point of grease for Twin ACSR MOOSE & Triple ACSR CONDOR | Refer Clause 1.1 of TECHNICAL SPECIFICATIONS, SECTION-VIIA, CONDUCTOR wherein IEC 61394/EN 50326 has been specified for grease. It is clarified that Type A grease as per above Standards shall be provided. |
|  | Cl 3.4.1.5 SECTION-I A (VOLUME-II), SS03 TL | As per the referred Clause, "Towers shall be designed such that the base width (C.G to C.G) at normal level (±0 m) does not exceed 7 (seven) m ". We understand that the above requirements are only for Suspension towers and not applicable all other tower types. Please confirm our understanding. | For 220kv line, Suspension & Tensions Towers shall be designed such that the base width (C.G to C.G) at normal level (± 0 m) does not exceed 7 (seven) m. For 400kv line, Suspension & Tensions Towers shall be designed such that the base width (C.G to C.G) at normal level (± 0 m) does not exceed 14 (Fourteen) m. |
|  | Supply BOQ-Schedule 1, Supply BOQ-Schedule 2, BOQ_Package TL01 & TL02.xlsx | We noticed that Basic Body quantities provided in supply and erection schedules are less, when compared to quantities of leg extension (given quantity/4.0). However, all the other supply items like insulators and hardware quantities are provided in line with Basic Body Quantities. Hence, We request to change the leg extension quantities in line with quantities of Basic Body of all tower types. | Bidders to quote as per BoQ and Technical Specification provided. |
|  | Supply BOQ-Schedule 1, Supply BOQ-Schedule 2, BOQ_Package TL01 & TL02.xlsx | We noticed that the total number of towers to be supplied are not in line with the quantities of foundations to be constructed. Hence, We request to verify the quantities and kindly provide us the final quantities. | Bidders to quote as per BoQ and Technical Specification provided. |
|  | Supply BOQ-Schedule 1, Supply BOQ-Schedule 2, BOQ_Package TL02.xlsx | We noticed that only Single Suspension Hardware fitting quantities are provided in the supply schedule. Requirement of double suspension fittings are necessary and required as per the terrain route conditions and Twin Moose Conductor requirements. Hence, We request to provide us the bifurcation of single suspension and double suspension hardware fittings for Twin ACSR Moose Conductor Transmission Line. | Bidders to quote as per BoQ and Technical Specification provided. |
|  | Cl:2.3.1, page-5 of 8, Sec-IA | As per the clause, Min ground clearance shall not be less than 8840mm (Min clearance at 1000 m above sea level, clearances at higher altitudes shall be submitted by the contractor to the client for approval.) Please provide the value of ground clearance for altitude up to 1500m & 3000m that should be considered by the contractor for designing. | a) Minimum Ground Clearance value for 400kV level line (For altitude up to 1500m ) : 9.1 m b) Minimum Ground Clearance value for 400kV level line (For altitude from 1500m to 3000m): 9.8 m c) Minimum Ground Clearance value for 220kV Line (For altitude upto 2000m): 7.3 m |
|  | Cl.1.6.2, Section IVD, Technical Specification Overload Factors for Open Type Foundation | As per Technical Specification clause 1.6.2 of Foundation Design (SECTION-IV D (VOLUME-II), Rev 0 (July’2022)), overload factor for open type foundation is given as 1.1. We understand that this factor is required for Stability & Strength checks of foundation design. Kindly confirm our understanding is correct. | Overload factor is to be taken in all checks of foundation design including Stability & Strength checks. |