|  | Section Project clause 6.2, Vol-II | # Meteorological data S. No; Name of Substation; 400/220 Bhadla-II PS & 400kV Bikaner-II PS;. 1; Snow Fall; Nil. 2; Wind Zone; As per National Building Code. 3; Seismic Zone; As per IS 1893. 4; Design Ambient Temperature; 50 degree centigrade. 5; Altitude; less than1000 meters above MSL. 6; Coastal Area consideration; NO ( However, Creepage requirement for insulators shall be 31 mm/ kV (min.). | Further to clarification no II Dated 22.02.2021, Please confirm that the creepage requirement for all the equipments is 25mm/ kv | Please refer Amendment no.-II. |
| --- | --- | --- | --- | --- |