|  |  | (Bhadla-II) |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | SAS Architecture | SAS Architecture | Please furnish existing SAS architecture for our necessary reference. | Available details/drawings shall be provided to successful bidder by POWERGRID during detailed engineering. |
|  |  | AC & DC Supply | AC & DC Supply | We presume that existing ACDB,DCDB, MLDB, ELDB shall have sufficient spares feeder modules and capacity to accomodate the present scope of work for proposed 400kV extension bays and New 220kB Bays. Hence, no augmentation works envisaged in existing AC & DC Distribution Boards. Please confirm. | Please refer sl. no. 9 of Amendment-I. |
|  |  | Illumination | Outdoor Power Receptacle for oil filtration unit (250A) | We presume that existing MSB has additional spare feeders to accomodate supply for Outdoor Power Receptacle for oil filtration unit (250A) board. Hence, no augmentation works envisaged in existing MSB Boards. Please confirm. | Kindly refer SPECIFIC REQUIREMENT’S (Section- Project)C/ENGG/SPEC/SEC- PROJECT/ SPECIFIC REQUIREMENT REV NO 04 Section: Switchyard Erection Rev 10 New Clause no. 20.4 for the same. |
|  |  | CRP & SAS | CRP & SAS | Kindly furnish/confirm the Exisiting relay make & model for CRP and SAS system. | Please refer sl. no. 3 & 4 of Amendment-I. |
|  |  | 400kV CRP Bus Bar Protection | 400kV CRP Bus Bar Protection | We understand that the Peripheral units required for Present bays are already available and our scope is only to use them in our relay panels along with necessary trip relays for augmentation of the existing busbar protection system. Please confirm. | Bus Bar Augmentation work as per section project clause no 3.1 c) i) is under present scope of work. |
|  |  | 220kV CRP Bus Bar Protection | 220kV CRP Bus Bar Protection | We understand that the Peripheral units required for Present bays are only to be supplied, no PU units for future bays shall be supplied under present scope of work. Please confirm. | Scope of work for new Bus Bar Along with PU for 220kV for present and future scope is as per SLD in conjunction with clause no 3.1 c) ii) of section project & Clause no 26 of section CRP rev 09 is under present scope of work. |
|  |  | PLCC/FOTE | PLCC/FOTE | As per BPS, PLCC, Analog Protection Coupler, HF Cable, Digital Protection Coupler, SDH or any type of telecom/teleprotection equipments supply is not indicated. Please confirm the same is not present scope. | Bidder to quote as per provisions of bidding documents. |
|  |  | Battery & Battery Charger | Battery & Battery Charger. | We presume that existing 220V & 48V battery & Charger have the sufficient capacity to cater the requirement of bays under present scope. Please confirm. | Please refer sl. no. 11 of Amendment-I. |
|  |  | VMS | VMS Augmentation | Please confirm that for VMS augmentation, supply and integration as per BPS is limited to local end only. Further, kindly provide the make and layout of existing VMS (Visual Monitoring system) in substation. | Confirmed. Available details/ drawings shall be provided to successful bidder by POWERGRID during detail engineering. |
|  |  | Erection Hardware | Erection Hardware | Erection hardware required for Tie bays are not indicated in the BPS. Kindly include the same. | Kindly refer typical module drawing C/ENGG/STD/Module attached with bidding documents for Tie bays. |
|  |  | Fire Fighting System | Fire Fighting System | Kindly specify the spare zone/window availability in the Existing fire alarm panel & Annunciation panel at control room building. | Available details/drawings shall be provided to successful bidder by POWERGRID during detail engineering. |
|  |  | Illumination Layout | Illumination Layout | We have considered outdoor lighting scope for the present scope of bays only. Outdoor illumination required for future bays are excluded from our scope of supply & engineering. Please confirm. | Confirmed, however bidder to quote as per BPS. |
|  |  | SAS Architecture | SAS Architecture | Please furnish existing SAS architecture for our necessary reference. | Please refer reply against clarification no.1 |
|  |  | (Bikaner-II) |  |  |  |
|  |  | Layout Plan | Layout Plan | Please furnish the existing plan layout | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS. |
|  |  | Trench Layout | Trench Layout | Please furnish the existing Trench and Civil foundation layout. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | Illumination Layout | Illumination Layout | Please furnish the existing illumination layout | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | SAS Architecture | SAS Architecture | Please furnish existing SAS architecture for our necessary reference. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | Cable Trench Layout | Cable Trench Layout | We understant that exisisting cable tranch (from CRB to present bay) is sufficient to accommodate the cable for present scope of work and bidders need to construct cable trench for present bays. Kindly confirm. Further, please furnish the existing trench layout. | Confirmed. As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | AC & DC Supply | AC & DC Supply | We presume that existing ACDB, DCDB, MLDB, ELDB shall have sufficient spares feeder modules and capacity to accommodate the present scope of work for proposed 400kV extension bays. Hence, no augmentation works envisaged in existing LT switchgear. Please confirm. | Confirmed. |
|  |  | Relay setting parameters | Relay seting parameters | Please confirm the relay settings parameters are to be furnished by PGCIL. | Confirmed. |
|  |  | Earthing BOQ | Earthing BOQ | Please furnish existing earth mat layout. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS. |
|  |  | CRP & SAS | CRP & SAS | Kindly furnish/confirm the Exisiting relay make & model for CRP and SAS system. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS. |
|  |  | 400kV CRP Bus Bar Protection | 400kV CRP Bus Bar Protection | We understand that the Peripheral units required for Present bays are already available in BB Spare relay panel, we shall use the same in relay panels to be supplied in present scope with necessary augmentation/integration to existing busbar protection system. Please confirm. | Confirmed. |
|  |  | SAS Architecture | SAS Architecture | We understand BCU shall be supplied for Present Line and Tie Bay only. BCU's for future bays under Present incomplete dia are not to be supplied. Please confirm. | Confirmed. |
|  |  | PLCC/FOTE | PLCC/FOTE | For telecommunication/Protection equipments are to be considered as per BPS only and supply/replacement/modification of panels/ equipments at remote end including power & control cabling are not covered under present scope of supply or services. Please confirm. | The Dismantling and shifting of existing PLCC panel shall be In line with TS section project cause 4.1.e) and respective item in mentioned in BPS sch -3 sl. No. 17. Bidder to quote as per BPS |
|  |  | PLCC/FOTE | PLCC/FOTE | Please indicate the make of PLCC/FOTE at remote end. | Available drawing/ document shall be provided during detailed engineering. |
|  |  | Visual Monitoring System (VMS) | Visual Monitoring System (VMS) | Please provide the make & layout of existing VMS in substation. | Available drawing/ document shall be provided during detailed engineering. |
|  |  | Firefighting System | Firefighting System | As per price schedule (BPS) and section project , any kind of HVWS piping extension and Deluge valve unit arrangement is not included in present scope of supply, Please confirm. | Confirmed. |
|  |  | Battery & Battery Charger | Battery & Battery Charger | We presume that existing 220V & 48V battery & Charger have the sufficient capacity to cater the requirement of bays under present scope. Please confirm. | Confirmed. |
|  |  | VMS Integration | VMS Integration | Please confirm that supply and integration of VMS augmentation as per BPS is limited to local end only. | Confirmed, however Bidder to quote as per provision of bidding documents. |
|  |  | Erection Hardware | Erection Hardware | Erection hardware required for Tie bays are not indicated in the BPS. Kindly include the same. | Please refer reply against similar query. |
|  |  | Fire Fighting System | Fire Fighting System | Kindly specify the spare zone/window availability in the Existing fire alarm panel & Annunciation panel at control room building. | Please refer reply against similar query. |
|  |  | Battery & Battery Charger | Battery & Battery Charger | We presume that existing 220V & 48V battery & Charger have the sufficient capacity to cater the requirement of bays under present scope. Please confirm. | Confirmed. |
|  |  | Civil Portion |  |  |  |
|  |  | BPS_Installation | LAND ACQUISTION / General | We assume that Land has been acquired by PGCIL. Please share the reference coordinates. | Bhadla-II Substation is already under construction and land for subject scope is already available, bidder may visit the site. Further, as Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | BPS_Installation | Approach Road | We have not envisaged the followings in our scope. • Area Clearance • Approach road illumination • Clearance of Local Authority and Statutory Bodies or any other similar bodies. | Kindly refer clause no 5.0 of Section project, specific exclusion. |
|  |  | BPS_Installation | Galvanising Thickness | Conforming to IS 2629 and as per site location with respect to coastal area we assume galvanising thickness of 610 g/m2 for all structural steel of 6 mm and above thickness, Kindly confirm our understanding. | As per cl 1.0 of Technical Specification, Section - Structure, all steel structures including anchor/foundation bolts shall be fully galvanized. The weight of the zinc coating shall be at least 610 gm/sq.m. |
|  |  | BPS_Installation | Water and Power | Please confirm, the distance of the location w.r.t. some reference point where point for water and power will be given to us. | Refer cl 14.3 of Technical Specification: Section: GTR. However, bidder is suggested to visit site for ready reference. |
|  |  | BPS_Installation | Foundation | In price schedule, Pile foundations has not been envisaged. In case, Pile is required based on Soil Investigation then, piling work should be treated as extra item. Please confirm. | Pile foundations are not envisaged at Bhadla-II. In case pile foundations are encountered at Bikaner-II, the same shall be dealt with as per cl 20.22 of Technical Specification: Section: Civil Works |
|  |  | BPS_Installation | Space for Site Office, Stores and Labour Camp | Space for the site office, stores and labour camp shall be provided to us near the area under present scope of works. Please confirm. | Based on availability of space at site, Site in charge shall earmark the space for site office, store and Labour camp to bidder. |
|  |  | BPS_Installation | General | In case, Extra items needs to be provided, same shall be paid as per market rates with overhead and other relevant factors. Please confirm. | For extra items if any during detailed engineering (i) if rates are available as unit item rates of BPS, same shall hold good, (ii) In case of new items the rate shall be derived from DSR in case of Scheduled items and in case of Non-Scheduled items standard practice of industry shall be followed. |
|  |  |  | 400kV CSD, 2nos required, item is not there | Please refer revised attached SLD and sl. no. 2 of Amendment-I. |
|  |  | ( Bhadla-II Civil) |  |  |  |
|  |  | General | Contour map | Kindly provide the existing contour map & FGL for existing Bhadla - II substation. | 1. Contouring map for Bhadla-II S/s shall be shared during detailed engineering. 2. Drawing indicating FGL for Bhadla-II S/s is enclosed. Refer sl. no. 17 in amendment-I. |
|  |  | General | Soil Investigation Report | Please provide the soil investigation report, which is required to identify the type of soil to be excavated. | Soil Investigation Report for Bhadla-II S/s is attached. Refer sl. no. 17 in Amendment-I. |
|  |  | Sch-3 , Civil Works , Item no. 112 | Railcum road (Four rail) | The drawing of Rail cum Road is found to be missing in the tender document. Request you to kindly provide the same. | Refer sl. no. 15 in Amendment-I. |
|  |  | Clause. 8.1.2- Substation Civil Works Rev- 11 A | Design Mix Concrete | "As per refered clause we understand that RCC M25 grade needs to procured from approved RMC plant confirm to IS 4926 or it needs to prepared using portable/mini/compact batching plant confirming to IS-4925". In absence of nearby RMC plants, we would like to use self loading concrete mixer machines complying to IS- 4926 for mixing the concrete, please confirm. | As per cl 8.1.2 of Technical Specification, Section: Civil Works: "Design mix concrete may be procured from approved RMC plant as per latest IS: 4926 or may be prepared by using a portable/mini/compact weigh batch plant conforming to latest IS: 4925". Hence any concrete mixer conforming to IS: 4925 for design mix concrete can be adopted. |
|  |  | Bikaner-I (Civil) |  |  |  |
|  |  | General | Contour map | Kindly provide the existing contour map & FGL for existing Bikaner - II substation. | Development of Bikaner-II S/s is in another package. The contour map and FGLs of the same shall be shared during detailed engineering. |
|  |  | General | Soil Investigation Report | Please provide the soil investigation report, which is required to identify the type of soil to be excavated. | Soil Investigation activity of Bikaner-II S/s is in another package. Soil Investigation Report of the same shall be shared during detailed engineering. |
|  |  | Sch-3 , Civil Works , Item no. 84 | Fence | The drawing of Fencing is found to be missing in the tender document. Request you to kindly provide the same. | Refer sl. no. 17 in Amendment-I. |
|  |  | Clause. 8.1.2- Substation Civil Works Rev- 11 A | Design Mix Concrete | The referred clause states that RCC M25 grade is to be procured from approved RMC plant which confirms to IS 4926 standards. Considering the small volume of RCC M25 grade as it is required only for Bay Extension Substations and also in the absence of availability of RMC Plants nearby to the area of Bay Extension, it is practically not feasible to provide batching plant. Alternatively, we request you to kindly allow the use of self loading concrete mixer machines complying to IS 4926 Standards for pouring of M25 Grade Concrete. | As per cl 8.1.2 of Technical Specification, Section: Civil Works: "Design mix concrete may be procured from approved RMC plant as per latest IS: 4926 or may be prepared by using a portable/mini/compact weigh batch plant conforming to latest IS: 4925". Hence any concrete mixer conforming to IS: 4925 for design mix concrete can be adopted. |
|  |  | Bhadla-II (Electrical) |  |  |  |
|  |  | Section-Switchgear-CB_Rev11 Cl. 2.6 & BHADLA-II 765-400-220KV SLD | The CSD shall be provided in Circuit breaker of switchable line reactor bay and in Main & Tie bay circuit breakers of Transformers, line with non switchable line reactors and Bus reactors. The CSD shall be supplied as per bid price schedules. | For 400kV Transformer bay, Control Switching Device for Main & Tie bay Circuit Breaker is mentioned in referred clause of Technical Specification as well as it is shown in the Single Line Diagram provided in the bidding document, However it is not included in the Supply price Schedule. Kindly confirm the requirement. | Please refer reply against clarification no 41. |
|  |  | BPS Sr. No. 16. & 18 | 245 kV, 2500A, 50KA, 1-Phase Current Transformer with 120% extended current rating. & 245KV, 1600A WITH 120% 1 PH (2 CORE) CT | Technical parameters/Core details for 245KV, 2500A CT & 245kV , 1600A 2 CORE CT ratios are not provided in the technical specification of Current Transformers. Kindly provide the technical parameters for the same. | Parameters are as under Sl. No.; Description; Ration; Accuracy class; Core. 1.; 1600A; 1600/1; 0.2S; 2. 2.; 2500A; 2500-1600-800/1; PX PX 0.2S PX PX; 5. Based on standard POWERGRID Design Philosophy and meeting the technical specification, other parameters shall be decided during detailed engineering. |
|  |  | Section project Bhadla-II; Cl. No. 3.1.d | Existing Fire alarm panel (i.e placed in FFPH building and control room building does not have provision for 400 kV class Auto Transformers. For the same “Fire alarm panel with all accessories” is considered is to be provided for complete scope and its integration with existing fire alarm panels | The Scope is not Clear. Kindly clarify if One no. of new Fire alarm panel is required for all the present bays under scope or only for present scope of 400kV class Auto transformer? Kindly Clarify the requirement. Also kindly furnish detailed drawings of existing fire alarm system; to estimate scope of integration of new fire alam panel. | Please refer sl. no. 5 of Amendment-I for scope clarity. Further available data and drawing shall be shared with bidder during detailed engineering. |
|  |  | BPS Sr. No. 20 & 82 | 245 kV, 1 phase Bus Post Insulator & Standard Pipe Structure for 220kV BPI | In Price shedule total Qty of 245kV Bus Post Insulator is given as 100 Nos. whereas Pipe structure of 245kV Bus Post Insulator are considerd for 76 Nos. Kindly clarify the exact requirment. | Please refer sl. no. 1 of Amendment-I. |
|  |  | Section project Bhadla-II; Cl. No. 3.1.B | Integration of IEC61850 communication based monitoring equipment like Optical temperature sensors, Digital RTCC etc and 400/220kV 3-Phase Autotransformer (to be supplied under a separate contract) with substation automation system is also included in the present scope. | Kindly provide the details for owner supplied 400/220kV 3-Phase Autotransformer & Optical temp. sensors / Digital RTCC etc. (make & model no. details.) to estimate integration scope of these communicatioin based monitoring equipments. | Available details/drawings shall be provided to successful bidder by POWERGRID during detail engineering. |
|  |  | Section project Bhadla-II; Cl. No. 3.1.C | Augmentation of existing 400kV bus bar protection: Any required modification in existing Busbar Protection of existing Main-I & Main-II for Protection and coordination with respect to sectionliser. | Kindly provide details of existing 400kV Bus Bar protection Panels (Type, make & model details.) | Existing 400kV bus bar, P741 (CU) & P743 (PU) are of M/s GE make |
|  |  | Section project Bhadla-II; Cl. No. 3.1.D | Fire protection system: HVW spray system and hydrant system for owner supplied 400/220kV Auto Transformers. Piping for the fire protection system shall be extended from the nearest header existing switchyard for this purpose. Augmentation of Fire detection & Alarm System for the Switchyard Panel Room, Transformers. | Kindly provide the detailed layout of fire hydrant system & Fire detection & Alarm system for existing substation as this is required for esitmation of extension of Hydrant system requirement. | Available details/drawings shall be provided to successful bidder by POWERGRID during detail engineering. |
|  |  | General | Installation of 400kV Bus Sectionalizer C&R panels | As per Bid Price Schedule there is provision of 5 SETs of Switchyard Panel Rooms (SPR). Our understanding is 1 no. SPR will be used for present scope of 400kV ICT bay C&R panels & 4 nos. SPR will be utilized for installation of 220kV C&R panels in new swithchyard. Kindly confirm whether our understanding is correct & also specify avalibility of space in existing 400KV SPR for installation of C&R panels of BUS SECTIONALIZER bays under present scope. | Requirement of Switchyard panels Room, shall be decided during detailed engineering based on best engineering practices. Bidder to quote as per BPS. |
|  |  | General | Sufficiency of existing LT Switchgear for bays under present scope | We understand that, for present scope, suffient AC & DC feeders are available in the existing LT switchgears & hence, there is no requirement of any augmentation of LT switchgear for present scope. Kindly confirm whether our understanding is correct. | Please refer sl. no. 9 in Amendment-I. |
|  |  | General | Conductor configuration for new 220kV Switchyard | As per tender Single Line Diagram 220kV Main bus - Quad Moose ACSR 220kV Transfer bus - Twin Bersimis ACSR. Kindly confirm the conductor configuration to be used in jack bus, equipment interconnections & dropers/jumpers for new 220kV Switchyard. | Interconnections, droppers/jumpers & jack bus for new 220kV Switchyard shall be of Twin Bersimis, however in bus Coupler bay same shall be of Quad Moose only. |
|  |  | Bikaner-II (Electrical) |  |  |  |
|  |  | General | Tentative Layout and Plot Co-ordinates for existing Bikaner-II substation. | Kindly provide tentative layout of existing substaion or furnish the distance from control room building to 400kV switch yard panel room to be considered for estimation of LT Power cables, SAS cables, & Fibre Optic cables required for present bays under scope. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | General | Sufficiency of existing LT Switchgear for bays under present scope | We understand that, for present scope, suffient AC & DC feeders will be available in the existing LT switchgears & hence, there is no requirement of any augmentation of LT switchgear for present scope. Kindly confirm whether our understanding is correct. | Please refer reply against clarification no 19. |
|  |  | General | Conductor configuration of existing 400kV Switchyard | Kindly furnish conductor configuration used for existing 400kV Switchyard for estimation of erection hardware items under present scope of augmentation work. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. However, bidder to match the conductor configuration at site. Bidder shall quote as per BPS |
|  |  | General | Earthmat | As per Bid Price Schedule, Main Earthmat is seperate line item. However, required risers are to be estimated by the bidders. Since the quantity of risers to be estimated is directly linked to Main Earthmat Spacing, we hereby request you to kindly provide the Earthmat Spacing in order to estimate the quantity of risers. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | Technical Specifications are to be provided |  | Please provide the Technical Specifications pertainig to following equipments. 1. SLD & Specifications for ACDB and DCDB extensions. 2. Conductor for Bus bar/Equipment Interconnections. | Available details/drawings shall be provided to successful bidder by POWERGRID during detail engineering. |
|  |  | Fire Alarm panel with all accessories | Sl. no 39. Schedule 1 Supply BOQ, EXTN 400/220KV BHADLA-II | Please confirm us the location of these Fire alarm Panels i.e at one of the New SPR or at main control room building so as to enable us to approximate the cable quantities for fire detection system | New Fire Alarm Panel shall be located at FFPH Building and Control Room building. |
|  |  | Fire Detection and Alarm System for Switchyard Panel Room of 6 mlength | Sl. no 48. Schedule 1 Supply BOQ, SS 64 EXTN OF BIKANER-II | We presume that the integration of these new fire detection and fire alarm system for SPR shall be connected with existing fire alarm panels. Please confirm. also confirm us the approximate distance between existing Fire alarm panels and new SPRs for cable quantity calculation purpose. | Confirmed. Distance shall be decided during detailed engineering abased on finalization of layout. The bidder to quote as per BPS |
|  |  | Control & Relay Panel and SAS |  | Please provide the existing makes of Control and Protection Scheme and SAS for both Substations | Available CRP at Bhalda-II Substation is of M/s GE/Siemens Make & SAS is of M/s SIEMENS Make. Further, for Bikaner-II, as PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS. |
|  |  | 400 kV & 220 kV Isolators. |  | Looking at the quantities of BPI as per price schedules, we presume that the all isolators shall be quoted alongwith cost of required BPI for each isolator. Please confirm. | Confirmed. |
|  |  | Type of Soil |  | As both the substations are exisitng, we request you to provide soil reports used for design of exsisitng foundations or please mentioned type of soil encountered at each substation so as as to consider excavation rates accordingly. | 1. Soil Investigation Report for Bhadla-II S/s is attached. Refer sl. no. 17 of Amendment-I. 2. Soil Investigation activity of Bikaner-II S/s is in another package. Soil Investigation Report of the same shall be shared during detailed engineering. |
|  |  | VMS |  | Please provide the existing makes of VMS system along with VMS Layout as per subject project scope | Available details/drawings shall be provided to successful bidder by POWERGRID during detail engineering. |
|  |  | Distance Between New SPR and Main control room building |  | We are considering the distance between Main control room building and New SPRs as 200 RM for calculation of Power Cable and OFC communication cable quantity estimation. | Bidder to quote as per provision of bidding documents. |
|  |  | (Bhadla-II) |  |  |  |
|  |  | Annexure-IV, Specific Requirement Rev03, S. No.: 77 | Transmission line side insulator string along with hardware for line termination shall be in the scope of substation contractor | Request to clarify whether line side hardware to be considered or not. | Confirmed. |
|  |  | Section Project Bhadla-II _ Bikaner-II, S. No.: 3.1 a) | 420kV & 245 kV Circuit Breakers along with support structures, Control switching device (CSD) | As per BPS there is no CSD for 400 & 220KV CB's whereas Section project indicated "420kV & 245 kV Circuit Breakers along with support structures, Control switching device (CSD)"_ please confirm the actual requirement. | Please refer sl. no. 2 of Amendment-I. |
|  |  | BPS-Supply : Sl.No :16,18,19 | 245 kV, 2500A, 50KA, 1-Phase Current Transformer with 120% extended current rating | We are unable to find specification details in pdf named as "4. Section-Switchgear-INST_rev11". It is requested provide the same. | Please refer reply against query no 51. Parameters for EVMT are as under Sl. No.; Description; Burden; Accuracy class; Core. 1.; 245kV; 50VA each core; 0.2; 2. Based on standard POWERGRID Design Philosophy and meeting the technical specification, other parameters shall be decided during detailed engineering. |
|  |  |  | 245KV, 1600A WITH 120% 1 PH (2 CORE) CT |  |  |
|  |  |  | 245KV, 1-PHASE METERING ELECTROMAGNETIC VOLTAGE TRANSFORMER (2 COREMETERING EMVT) |  |  |
|  |  | Bid Price schedule-1, NIT SS-64 EXTN 400/220KV BHADLA-II BoQ, Sl.no.49 - | COLOR IP CAMERA, WITH PAN, TILT AND ZOOM FACILITIES, ALONGWITH ALLREQUIRED ITEMS, ACCESSORIES, LINE INTERFACE UNITS, FIBER PATCH CORDS,POWER SUPPLY UNITS, JUNCTION BOXES, CABLES, FIBER OPTIC CABLES, ETC.,AND INCLUDING INTEGRATION IN EXISTING HARDWARE AND SOFTWARE FORAUGMENTATION OF VISUAL MONITORING SYSTEM AS PER TECHNICALSPECIFICATION. | a) Please specify the make of the existing Visual Monitoring System for 400/220KV BHADLA-II. b) It is requested to provide the quantity of cameras to be required. c) For Augmentation of existing VMS, request to provide the VMS layout of existing BHADLA-II for estimating the new cable and other accessories required for integration of new VMS with Existing | a) Please refer reply for similar query. b) Bidder to quote as per provision of bidder documents. c) Available details/drawings shall be provided to successful bidder by POWERGRID during detail engineering. |
|  |  | Section Project Bhadla-II | General | Creepage distance are mentioned as 25mm/kV and 31 mm/kV at different places of the TS. Please confirm what is to be considered for Bhadla-II Substations. | Kindly refer clause no 6.2 for Creepage, wherein 31mm/kV to be considered for both substations. |
|  |  | Section Project Bhadla-II | General | Please provide the details of existing DSLP. | Available details/drawings shall be provided to successful bidder by POWERGRID during detail engineering. |
|  |  | Section Project Bhadla-II | General | We understand that the required no of peripherals/ports for Bus Bar Integration are available. Please Confirm. | Kindly refer clause no 3.1.c of section project for scope of work. Bidder to quote as per provision of Bidding documents. |
|  |  | BPS Schedule-1, sl. No. 37 | Fire Detection and Alarm System for Switchyard Panel Room of 6m length | We will consider Conventional Type Fire Detection & Alarm System for Switchyard Panel Rooms. Please confirm | Confirmed. |
|  |  |  |  | We assume that there is the Provision/windows in the Existing FDA cum Annunciation panel located in the Existing Control Building to take the FDA Signal of Switchyard Panel Room. So, New FDA panel at CRB is not required. Please confirm | Please refer reply for similar query. |
|  |  |  |  | We assume that there is Provision in the SCADA to have signals of AC system and Fire-fighting system as per TS. please confirm. | Bidder to quote as per provision of Bidding documents. |
|  |  |  |  | Please provide the exiting Fire- fighting alarm layout & SLD drawings. | Available details/drawings shall be provided to successful bidder by POWERGRID during detail engineering |
|  |  | Section Project Bhadla-II _ Bikaner-II, | Make and Model of Existing Bus bar protection will be provided during detailed engineering | Request PGCIL to provide tentative make and model of bus bar protection for tender purpose to bring all the bidders on to a common platform. | Please refer reply for similar query sl no 55. |
|  |  | Section Project Bhadla-II _ Bikaner-II, | Make and Model of SAS will be provided during detailed engineering | Request PGCIL to provide tentative make and model of SAS for tender purpose to bring all the bidders on to a common platform | Please refer reply for similar query sl no 67. |
|  |  | Section Project Bhadla-II _ Bikaner-II, | Fire protection system: HVW spray system and hydrant system for owner supplied 400/220kV Auto Transformers. Piping for the fire protection system shall be extended from the nearest header existing switchyard for this purpose | Please confirm the following Points: 1. Please provide the Existing Fire Hydrant layout drawing which showing Existing Fire Pipe header and tapping point which can be extended for Hydrant system. In the Absence of the same, We will consider 50 m tapping distance from existing header. 2. We assume that Existing Pumping Capacity, Pump head and water tank capacity is sufficient to take care the Hydrant system for BHADLA-II Ext. Hence Fire Pumping system is totally excluded from Bidder scope of work. Please confirm. 3. Yard piping shall be designed by following NFPA/IS code with hydraulic calculations | - Bidder to visit site for get acquainted. Bidder to quote as per provision of bidding documents. - Confirmed. - Bidder to quote as per provision of bidding documents. |
|  |  | Section Project Bhadla-II _ Bikaner-II, | EXTN OF Bhadla-II | Please furnish the following details of existing 400kV & 220KV switchyard: a) Location of control & relay panel - Control building / AC kiosk b) Type of 400kV& 220KV Main Bus - Rigid / Flexible c) Type & configuration (Twin or Quad) of 400kV & 220KV Main Bus conductor | - Bidder to visit the site for get required inputs. - Main bus are Flexible Type. - Quad Bull for 400kV and Quad Moose for 220kV. |
|  |  | General | Order of precedence | In case of discrepancy between price schedule & section-project, Please clarify the order of precedence. | Please refer provisions of Bidding Documents at ITB 22.3.2 |
|  |  | General | General | We presume that the price of support insulators for outdoor AIS isolators shall be included in the respective line item of isolators only. Please confirm | Please refer reply of similar query sl no 68. |
|  |  | General | General | We presume that Earthing, DSLP, Lighting, Cable trench & other associated works are required to be executed only for the present scope of works and the same are not required for future bays. Please confirm. | Confirmed |
|  |  | General | General | We understand that control and protection panel for Bhadla & Bikneer-II substations shall be placed in respective bay AC kiosk only. Please confirm | Confirmed, however SAS panel shall be at Control room. |
|  |  | ( BIKANER-II ) |  |  |  |
|  |  | Section Project Bhadla-II _ Bikaner-II, | EXTN OF BIKANER-II | Kindly provide following details for bay extension works at BIKANER-II station: a. Overall Layout of Switchyard b. Control building layout c. Earthing Layout / Earth mat spacing. d. Cable trench layout (Indoor & outdoor). e. DSLP layout f. VMS Layout | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | Section Project Bhadla-II _ Bikaner-II, | EXTN OF BIKANER-II | Please furnish the following details of existing 400kV switchyard: a) Location of control & relay panel - Control building / AC kiosk b) Type of 400kV Main Bus - Rigid / Flexible c) Type & configuration (Twin or Quad) of 400kV Main Bus conductor | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS. However, bidder to match conductor configuration to main package configuration. |
|  |  | Section Project Bhadla-II _ Bikaner-II, | EXTN OF BIKANER-II | As BIKANER-II substation is also under Bidding/execution stage, we presume that the following auxiliary system being supplied under a separate contract are adequately rated to cater the requirement of the bay extensions proposed in this package. a) 220V and 48V Battery & charger b) LT Transformer c) DG d) ACDB & DCDB with adequate spare feeders -Please confirm. | Confirmed. |
|  |  | Section Project Bhadla-II _ Bikaner-II, S.No : 4.1 C) | In the present scope, bidder will provide BCUs required for 400 kV bays including all necessary hardware and software to integrate with the existing Substation Automation System | We understand that any additional gateways requirement for sending data to remote end is not envisaged for both substations. Existing gateways shall have capability to cater local substation data. Please confirm. | Bidder to quote as per provision of Bidding documents. |
|  |  | Section Project Bhadla-II _ Bikaner-II, S.No : 4.1 o) | VMS | As per referred clause, the bidder shall provide 2 sets of color IP camera with PAN, TILT and ZOOM facilities suitably located in the switchyard for monitoring of bays and equipment. We understand that, if the number of cameras are increased during detail engineering, then the same shall be paid additionally. Please confirm. b) Augmentation of Visual monitoring system is not mentioned in the section project. Please check and confirm the scope of work. c) Please furnish the Make and Model number of existing VMS system | Bidder to quote as per provision of bidding documents. |
|  |  | Section Project Bhadla-II _ Bikaner-II, S.No : 4.1 p) | FO based Communication Equipment shall include planning, designing, engineering, supply, transportation, insurance, delivery at site, unloading handling, storage, installation, termination, testing, training and demonstration for acceptance, commissioning and documentation | As per referred clause & price schedule, New FOTE system shall be provided at BIKANER-II station for present 400kV lines direction. In this regard, please clarify whether proposed new FOTE need to be integrated with the existing FOTE. If required, Please furnish the following details: a) Make & model no. of existing FOTE. | New FOTE system to be supplied under the present scope shall be integrated with the existing equipment (if any). Bikaner -II S/S is stii under award, so make & model of existing FOTE is not known |
|  |  | Section Project Bhadla-II _ Bikaner-II, S.No : 4.1 p) v) | Integration with the existing communication system based on SDH and PDH of employer. | Please provide the make / model of existing SDH & spare ports availability for integration at both end substations. | The existing SDH at Bhadla-II is Tejas make TJ1400 model equipment. Spare port is available in the existing equipment at BHadla-II for integration. Bikaner-II S/s is still under award so make & model of existing SDH equipment is not known. |
|  |  |  |  | As per price schedule only SDH Equipment is required to be offered & no PDH Equipment is required. Also Integration with existing equipment is to be done at Electrical level (E1 & Ethernet), integration at PDH level not required as PDH equipment not to be offered. Please confirm . | Integration with existing SDH equipment is to be done at optical level. New PDH equipment is not required in the present scope, however, it may be required to integrate existing PDH equipment with the new supplied SDH equipment at E1 level. |
|  |  | Section Project Bikaner-II, | PMU scope | Please furnish a conceptual diagram for PMU scheme indicating the following: a) Stations connected through FO link b) Distance between each link c) Transmission capacity for each link d) Scope demarcation between new and existing SDH equipments | Bidder to comply requirement mentioned in the TS. |
|  |  | Section Project Bikaner-II, | OPGW Joint box at Line terminal Gantry | We have not considered OPGW Joint box (at the Substation end) for terminating the OPGW cables supplied and installed along with the transmission lines. The same shall be under Transmission Line scope | Supply of joint box is not envisaged in the present scope of bid. |
|  |  | Section Project Bikaner-II, | General | Creepage distances were mentioned as 25mm/kV and 31 mm/kV at different places of the TS. Please confirm what is to be considered for Bikaner-II Substation. | Please refer T.S Section Project Clause 6.2 - Creepage requirement for insulators shall be 31 mm/ kV (min.) |
|  |  | Section Project Bikaner-II, | General | Please provide the details of existing DSLP. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | Section Project Bikaner-II, | General | We understand that the required no of peripherals/ports for Bus Bar Integration are available. Please Confirm | Confirmed. |
|  |  | Section Project Bikaner-II, | General | As wave traps are used in the present scope, request PGCIL to provide details of existing PLCC make and Model for integration of present scope with existing. | Requisite drawing/ document shall be provided during detailed engineering to the successful bidder. |
|  |  | (Bhadla-II) |  |  |  |
|  |  | clause no.- 2.1.3/section project bhadla-II & bikaner-II | Only Supply, erection, testing and commissioning of one (1) no. 500MVA, 400/220/33kV Three Phase Auto transformers at 765/400/220 kV Bhadla-II (Extn.) PS are covered under separate package. However all associated work such as connection to switchyard bay, HVWS & Hydrant Protection of Auto transformers, power & control cabling (from common Marshaling box of bank/Marshalling box of three phase unit, OLTC to RTCC panel (Except special cable), civil work etc are under present scope of work | we understand that the supply, erection, testing & commissioning of 500MVA 400/220/33KV three phase auto tranformer are not under present scope. Only connection to switchyard bay,, HVWS & Hydrant Protection of Auto transformers, power & control cabling (from common Marshaling box of bank/Marshalling box of three phase unit, OLTC to RTCC panel (Except special cable), civil work etc are under present scope of work.Pls. conform our understanding. Pls. provide the GA dwg. of 500MVA power trafo | Confirmed. Requisite drawing/ document available shall be provided during detailed engineering to the successful bidder. |
|  |  | Clause no.-3.J/section project | The Earthmat in the existing switchyard is being laid in a separate package. Spacing details shall be shared during detailed Engineering. Extension of the same wherever required shall be carried out with same spacing as existing spacing. Main Earthmat is to be quoted as per BPS on unit rate basis | We understand that the Laying of Main earthmat shall be not under present scope for present scope of work. ONLY riser connection from Main eartmat to equipments & auxiliary earthmat shall be under prsesent scope of work.However There is discrepancy between section project & BPS. In section project it is mentioned that the MAIN EARTHMAT is being laid in seperate package but in BPS length of 40MM MS ROD Main earthmat has been mentioned i.e 8KM. Pls. conform our understanding. Kindly provide the spacing details & ERT reports . | Kindly refer already attached earthmat layout with bidding documents for existing/extn scope of work, spacing etc. |
|  |  | General |  | We are not considering extension of AC DC board ,MSB,ELDB,MLDB under present scope. We are assuming that existing AC DC borad have sufficient feeder available for supply to present scope for extension of 400KV bays & 220KV bays line bays panel.Hence we are not considering any separate LT borad/augmentation work for present bay panel supply.Please confirm our understanding | Please refer reply for similar clarifications. |
|  |  | Section Project,clause no.- 3.1/b | integration of IEDs under present scope of augmentation with existing substation automation (which is based on IEC 61850) and compatibility enhancement of same as required including hardware (if any required), updating of system database, displays, development of additional displays and reports as per requirement. | Please provide the Existing SAS(make & model number) sytem make details for considering the augmentation work for present scope bays | Please refer reply for similar clarifications. |
|  |  | Section Project,clause no.-3.1/c | Supply & installation of New Busbar protections i.e. Redundant (1+1) numerical low impedance biased differential Bus Bar protection scheme for each Main bus i.e. both 400kV Main-I & Main-II bus sections which is created by Bus sectionlisers as per Section Control and Relay Panel of the Technical Specifications. Same shall be for all bays (Present, existing as well as future bays as shown in SLD) of section for which Busbar protection is provided by contractor | we understand that the Bus bar protection panel is already present in existing substation .only augmentation shall be under present scope of work. In same way we understand that the present scope of bays panel ,existing bays panel, future bays panel are already existing in substation . only augmentation related works for prsenet scope of bays,existing bays panel & future bays panel which are marked in bubbled circle as per tender SLD shall be under present scope of work.Pls. conform our understanding . Please provide the Existing busbar protection sytem scheme(i.e centralised or distributed) make details for considering the augmentation work for present scope bays | Scope of work clearly defined in section project clasue no 3.1 c. Bidder to quote as per provision of bidding documents. |
|  |  | General | Battery & battery charger system | We are assuming that existing battery is sufficient to catter the DC requirement of present scope bay. Hence we have envisaged not any new battery system for the same. Please confirm our understanding | Please refer sl. no. 11 of Amendment-I. |
|  |  | General |  | we are not considering any fote equipments under preent scope of work. Pls. conform it | Confirmed. |
|  |  | General |  | we are not considering any remote end activities in present scope except only PLCC & its related integration work.Pls. conform our understanding | Confirmed. |
|  |  | General |  | Pleas provide the Existing VMS information about server and software (make and licenses) | Please refer reply for similar clarifications sl no 9. |
|  |  | Section Project,clause no.- 3.1/e | SPR(6M length) | we are considering NOS.-5 SPR as per BPS.We have considered NOS.-1 SPR(6M) for each 400KV full dia bays & remaining SPR(6M) for remaining 220KV bays. | Please refer reply for similar clarifications sl no 57. |
|  |  | General | Section Dwg | kindly provide the tender section & layout Dwg in autocad format for existing substation | Requisite drawing/ document available shall be provided during detailed engineering to the successful bidder. |
|  |  | General | cable trench | can we use the existing trench(indoor & outdoor) for laying the cables for under present scope of work OR we have to make seperate trench(outdoor& indoor) upto ontrol room building. Pls. Conform our understanding. kindly provide the existing trench layout( indoor & outdoor) dwg. | Exiting outdoor foundation cum trench layout is already attached with bidding documents. Bidder to examine the requirement of addition cable trenches. Further, Bidder to quote as per provision of bidding documents. |
|  |  | General | control room building | kindly provide the layout dwg. of existing control room building,panel arrangement details & also provide the distance of control room buidling from present scope of bays. | Requisite drawing/ document available shall be provided during detailed engineering to the successful bidder. |
|  |  | General |  | can we placed relay panels under present scope of work in existing SPR/control room building. Pls. conform it | Bidder to quote as per provision of bidding documents. |
|  |  | General |  | we understand that the existing bus bar protection panel of 400KV & 220KV have already PU units for our present scope of bays. hence we dont need to consider another bus bar protection panel.Pls. conform our understanding | Bidder to quote as per provision of bidding documents. |
|  |  | General |  | kindly provide the existing illumination layout | Requisite drawing/ document available shall be provided during detailed engineering to the successful bidder. |
|  |  | Section Project, clause no.- 3.1/a |  | We understand that PLCC equipments, Augmentation work in Fote equipments are not under present scope. Only wavetraps (pedestal mounted) shall be under present scope of work. Pls. conform our understanding | Confirmed. |
|  |  | General |  | as we understand that the this bhadla substation 400/200KV BHADLA EXTN. Work is cioming under the same substaion(765/400/220KV bhadla-II under part-b,part-c & part-E for which tender engineering had been done. Pls. conform our understanding | Bidder to quote as per provision of bidding documents. |
|  |  | General | PLCC | As we understand that the PLCC equipments at bhadla-II shall be dismantled, shifted to bikaner-PS & PLCC equipments at bikaner-II PG shall be dismantled, shifted to bhadla-II & also covers all integrated related works for PLCC equipments. Pls. conform our understanding | Not related to Bhadla-II S/s. |
|  |  | Section Project, clause no.- 3.3/I/C | Roads | we understand that the road activities shall be under present scope as per GA dwg. however there is discrepancy between GA dwg & existing layout, in existing layout existing roads are already shown for present scope of 400KV & 220KV bays. Pls conform our understanding | Bidders to visit site for get required inputs. |
|  |  | General | Bus works for main bus-I & bus-II | since the ICT-6 bay is at the cornermost as per GA dwg. which is under present scope of 400KV bays so we understand that the extension of bus works shall be upto ICT-6 bay. Pls. conform our understanding | Extension of Main bus-I, Main bus-II and jack buses upto to 6th ICT are in scope of bidder and shall be paid under item of “Erection Hardware for 400kV I type layout-Bus Work (For two diameters)as per technical specification” unit wise. |
|  |  | Section Project, clause no.- 2.2.1 |  | 1.we are considering only 400KV ICT-6 & its associated activities under present scope as per section project. 2. we are not considering 400KV ICT-7,400KV ICT-8,400KV LINE-2(F) & its asociated activities(tower, beam) under present scope as per GA dwg. please conform our understanding | Bidder to quote as per provision of bidding documents. |
|  |  | General | Bus coupler bay, 400/220KV ICT-8 | 1.please marked the location of 220KV B/C bay in tender GA dwg. since location has been not mentioned. 2. we understand that the 220KV ICT-8 & its associated activities(tower beam) are not under present scope as per tender GA dwg. Pls. conform our understanding | Bus & TBC Bay shall be in same bay space. However, for other activities Bidder to quote as per provision of bidding documents. |
|  |  | Civil |  |  |  |
|  |  | General |  | Kindly provide the topographical data for Earthwork Computation. | 1. Contouring map for Bhadla-II S/s shall be shared during detailed engineering. 2. Drawing indicating FGL for Bhadla-II S/s is enclosed. Refer sl. no. 17 of Amendment-I. |
|  |  | General |  | Kindly provide soil investigation report for computation of foundation work. | 1. Soil Investigation Report for Bhadla-II S/s is attached. Refer sl. no. 17 of Amendment-I. 2. Soil Investigation activity of Bikaner-II S/s is in another package. Soil Investigation Report of the same shall be shared during detailed engineering. |
|  |  | Price schedule |  | Kindly provide foundation details of exsisting structures for Estimation of dismentaling BOQ. | Dismanlting of RCC is in unit rate. The bidder to qoute as per BPS. |
|  |  | General |  | As per scope of work we understand that only SPR is in the Bidder scope, same is mentioned in the price schedule, kindly confirm the same. | Scope of work is elaborately defined in the Section Project. Bidder to qoute as per BPS. |
|  |  | General |  | As per Volume II part 1 section project- Clause No. 3.3.IV, Factor of safety considered for design of foundation of Tower & Equipment is 1.5 for both Normal & Short circuit condition whereas in technical specification- Clause No. 10.5.3, it is 2.2 for normal condition & 1.65 for short circuit condition. Kindly clarify the same. | Section Project supersedes Technical Specification: Section - Civil Works. Hence Factor of Safety's mentioned in Section Project shall prevail. |
|  |  | Bikaner-II |  |  |  |
|  |  | Clause no.-4.1/b/section project | 400kV Bus bar protection scheme (Duplicate) at Bikaner-II PS is being provided in separate contract for the bays under present scope. However, necessary modification, wiring/cabling, shifting, installation and integration of same for completion of 400kV Bus Bar protection is under present scope and same is to be quoted under respective item available in Installation schedule of BPS. | As per the given claise we understand that the supply of 400KV bus bar protection scheme(duplicate) is not under present scope. Only necessary associated works like installation, integration of same for completion of 400KV bus bar protection is under present scope.Pls. conform our understanding | Confirmed |
|  |  | Clause no.-4.1/L/section project | The Main Earthmat shall be extended for the switchyard area under present scope of work. All the equipment, structures, cable trenches, auxiliary Earthmat for isolators etc. shall be earthed by connecting them to the main Earthmat. | As per our understand Main earthmat shall be under present scope. Pls. provide the existing Earthmat layout & spacing,ERT reports for further work. Pls. conform our understanding | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | General | layout | As per our understanding Layout shall be as per the tender SLD. Pls. conform it. Pls. provide the existing layout,SLD,section,cable trenches route, control room building location,main earthmat layout for further necessary work | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | General | SPR- 6M length | we have considered NOS.-1 SPR(6M length) for each full dia 400KV bays. Pls. conform our understanding | Confirmed |
|  |  | General | control room building | As per our understanding Control room building is already existing. So we have not considered for the same. | Confirmed |
|  |  | General | GA DWG. | As per tender GA,we understand that extension of Main bus-I & Main bus-II for two 400KV full dia bays are under present scope as per the tender SLD.Please confirm our understanding | Confirmed |
|  |  | General |  | We are not considering extension of AC DC board,MSB,ELDB,MLDB under present scope.We are assuming that existing AC DC borad have sufficient feeder available for supply to present scope for extension of 400KV bays panel.Hence we are not considering any separate LT borad/augmentation work for present bay panel supply.Please confirm our understanding | Confirmed |
|  |  | Section Project,clause no.- 4.1/c | integration of IEDs under present scope of augmentation with existing substation automation (which is based on IEC 61850) and compatibility enhancement of same as required including hardware (if any required), updating of system database, displays, development of additional displays and reports as per requirement. | Please provide the Existing SAS sytem( make & model no.) details for considering the augmentation work for present scope bays | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | Section Project,clause no.-4.1/c | The Scope of bidder shall include but not be limited to integration of IEDs under present scope of augmentation with existing substation automation (which is based on IEC 61850) and compatibility enhancement of same as required including hardware (if any required), updating of system database, displays, development of additional displays and reports as per requirement. | Please provide the Existing busbar protection sytem make details for considering the augmentation work for present scope bays | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | General | Battery & battery charger system | We are assuming that existing battery is sufficient to catter the DC requirement of present scope bay.Hence we have envisaged not any new battery system for the same.Please confirm our understanding | Confirmed |
|  |  | Section Project,clause no.-4.3/1/d | switchyard fencing | Fencing of switchyard shall be for present scope of work only as per the tender GA dwg. Pls. conform our understanding | Confirmed |
|  |  | Section Project,clause no.-4.1/O | Augmentation of Visual Monitoring System (VMS) for switchyard area under present scope. | Pleas provide the Existing VMS information about server and software (make and licenses) | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | Section Project,clause no.-4.1/q | The broad Scope of the procurement of PMU shall include planning, design, engineering, supply, transportation, insurance, delivery at site, unloading handling, storage, installation, termination, testing and demonstration for acceptance, commissioning and documentation for PMU as per BPS at –Bikaner II PS and these PMU shall support IEEE C 37.118 protocols. These PMUs shall be integrated with Phasor data Concentrator (PDC) at RLDC/SLDC for the subject project. | Please provid the Existing Phasor data Concentrator (PDC) at RLDC/SLDC details | The requisite details shall be provided during detailed engineering to the successful bidders. |
|  |  | Section Project,clause no.-4.1/p/Vii | Integration of new Communication equipment in the existing regional NMS. All required support to existing NMS vendor for integration of new Communication equipment | Please provide the Existing regiona NMS communication details for Integration of new Communication equipment in the existing regional NMS. | The requisite details shall be provided during detailed engineering to the successful bidders. |
|  |  | General | Section Dwg | kindly provide the tender section & layout Dwg in autocad format for existing substation | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | General | cable trench | can we use the existing trench(indoor & outdoor) for laying the cables for under present scope of work OR we have to make seperate trench(outdoor& indoor) upto ontrol room building. Pls. Conform our understanding.kindly provide the existing trench layout(indoor & outdoor) dwg. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | General | control room building | kindly provide the layout dwg. of existing control room building,panel arrangement details & also provide the distance of control room buidling from prsent scope of bays. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | General |  | can we placed relay panels under present scope of work in existing SPR/control room building. Pls. conform it | The bidder to provide SPR under present scope as per BPS. |
|  |  | General |  | As we understand the PU units is already avalbale for existing bus bar protection for present scope of bays. Pls conform our understanding | Confirmed |
|  |  | General |  | kindly provide the existing illumination layout | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  |  |  | as we understand that the this bikaner substation 400KV EXTN. Work is part of bikaner-II substation(package-F) for which tender engineering has been done.Pls. conform our understanding. | As Bikaner -II PS is being developed under separate package and under present scope extension of 400 KV Bikaner - II PS is envisaged as per TS section project clause no. 2.2. |
|  |  | Section Project,clause no.-4.1/e | PLCC | as we understand that the 400KV line bikaner-II PS is connected to bhadla-II & 400KV line bikaner-II PG is connected to Bhadla-II in current situation. As per the present scope of work 400KV line Bikaner-II PG will be connected to bikaner-II PS. Also we understand that PLCC of BIKANER-II PG will be dismantled, shifted to bhadla-II & PLCC equipments of bhadla-II will be dismantled, shifted to bikaner-II PS . Also new PLCC equipments(supply,integration) at bikaner-II PG shall be placed under present scope of work to make bikaner-II PS to bikaner-PG 400KV line . Pls. conform our understanding. | For clarity in scope of PLCC for Extn. In Bikaner-II PS please refer TS section project Clause 4.1.e) |
|  |  | scope of work |  | kindly marked the location of NOS.-2 400KV full dia bay under present scope of bays as per section poject in existing layout Dwg. Pls. provide the existing layout dwg. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | Civil |  |  |  |
|  |  | General |  | Kindly provide the topographical data for Earthwork Computation. | 1. Contouring map for Bhadla-II S/s shall be shared during detailed engineering. 2. Drawing indicating FGL for Bhadla-II S/s is enclosed. Refer sl. no. 17 of Amendment-I. |
|  |  | General |  | Kindly provide soil investigation report for computation of foundation work. | 1. Soil Investigation Report for Bhadla-II S/s is attached. Refer sl. no. 17 of Amendment-I. 2. Soil Investigation activity of Bikaner-II S/s is in another package. Soil Investigation Report of the same shall be shared during detailed engineering. |
|  |  | Price schedule |  | Kindly provide foundation details of exsisting structures for Estimation of dismentaling BOQ. | Dismanlting of RCC is in unit rate. The bidder to qoute as per BPS. |
|  |  | General |  | As per scope of work we understand that only SPR is in the Bidder scope, same is mentioned in the price schedule, kindly confirm the same. | Scope of work is elaborately defined in the Section Project. Bidder to qoute as per BPS. |
|  |  | General |  | As per Volume II part 1 section project- Clause No. 3.3.IV, Factor of safety considered for design of foundation of Tower & Equipment is 1.5 for both Normal & Short circuit condition whereas in technical specification- Clause No. 10.5.3, it is 2.2 for normal condition & 1.65 for short circuit condition. Kindly clarify the same. | Section Project supersedes Technical Specification: Section - Civil Works. Hence Factor of Safety's mentioned in Section Project shall prevail. |
|  |  | (Bhalda-II) |  |  |  |
|  |  | BPS, Schedule-1, sl. No. 37 | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length-5 Set | We will consider Conventional Type Fire Detection & Alarm System for Switchyard Panel Rooms. Please confirm | Please refer reply against query no 79. |
|  |  | Section Project, Clause no, 3.1-d | Existing Fire alarm panel (i.e placed in FFPH building and control room building does not have provision for 400 kV class Auto Transformers. For the same “Fire alarm panel with all accessories” is considered is to be provided for complete scope and its integration with existing fire alarm panels. | As per refered clause, New Fire Alarm panel to be intergrated with with Existing Fire Alarm Panel. We assume that there is the Provision in the Existing FDA cum Annunciation panel for intergration with new Fire Alarm Panel. Please confirm. Further, Please provide the detail/Make etc. of Existing Fire Alarm Panel. | Please refer sl. no. 5 of Amendment-I. Available details/drawings shall be provided to successful bidder by POWERGRID during detailed engineering. |
|  |  | Section Project, Clause no, 3.1-d | Fire protection system: HVW spray system and hydrant system for owner supplied 400/220kV Auto Transformers. Piping for the fire protection system shall be extended from the nearest header existing switchyard for this purpose. Augmentation of Fire detection & Alarm System for the Switchyard Panel Room, Transformers. | Please provide the Existing Fire Hydrant layout drg showing Existing Fire Pipe header and tapping point location, which can be extended for HVWS & Hydrant system. | Please refer reply against query no 82. |
|  |  | Section Project, Clause no, 3.1-d | Fire protection system: HVW spray system and hydrant system for owner supplied 400/220kV Auto Transformers. Piping for the fire protection system shall be extended from the nearest header existing switchyard for this purpose. Augmentation of Fire detection & Alarm System for the Switchyard Panel Room, Transformers. | We assume that Existing Pumping Capacity, Pump head and water tank capacity is sufficient to take care the HVWS & Hydrant Fire fighting system. Hence Fire Pumping system or Booster Pumping System is totally excluded from Bidder scope of work. Please confirm. | Please refer reply against query no 82. |
|  |  | Section Project, Clause no, 3.1-d | Fire protection system: HVW spray system and hydrant system for owner supplied 400/220kV Auto Transformers. Piping for the fire protection system shall be extended from the nearest header existing switchyard for this purpose. Augmentation of Fire detection & Alarm System for the Switchyard Panel Room, Transformers. | We assume that there is the provision in the existing DCDB Panel located in the existing Fire Pump house & Main Control Room building to provide DC power in the deluge valve panels for HVWS spray system. So DCDB panels are not required separately. Please confirm. | Confirmed. |
|  |  | Section Project, Clause no, 3.1-d | Fire protection system: HVW spray system and hydrant system for owner supplied 400/220kV Auto Transformers. Piping for the fire protection system shall be extended from the nearest header existing switchyard for this purpose. Augmentation of Fire detection & Alarm System for the Switchyard Panel Room, Transformers. | We are considering tapping distance from existing header as 50 metres. Please provide the exact length of tapping to be considered for the extension of Hydrant/ HVWS system. | Please refer reply against query no 82. |
|  |  | Section Project, Clause no, 3.1-d | General | Pls provide the exiting Fire fighting alarm system layout & SLD dwgs. | Please refer reply against query no 82. |
|  |  | Section Project, Clause no, 3.1-d | General | Pls provide the existing Indoor and outdoor cable trench layout dwg | Available details/drawings shall be provided to successful bidder by POWERGRID during detailed engineering. |
|  |  | TECHNICAL SPECIFICATION FOR FIRE FIGHTING SYSTEM & AIR CONDITIONING SYSTEM | General | We assume that there is Provision in the SCADA to have signals of AC system and Fire fighting system as per TS. pls confirm. | Bidder to Quote as per provision of bidding documents. |
|  |  | TECHNICAL SPECIFICATION FOR AIR CONDITIONING SYSTEM, | General | Air- Conditioning heat load calculation shall be done on the basis of max site temperature( 45 deg C) and unit will statisfactory work upto ambient temperature i.e. 50 deg C.Please confirm. | Bidder to Quote as per provision of bidding documents. |
|  |  | BPS, Schedule-1, sl. No. 37 | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length-5 Set | We will consider Conventional Type Fire Detection & Alarm System for Switchyard Panel Rooms. Please confirm | Please refer reply against query no 79. |
|  |  | Bikaner-II |  |  |  |
|  |  | BPS, Schedule-1, sl. No. 48 | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length | We will consider Conventional Type Fire Detection & Alarm System for Switchyard Panel Rooms. Please confirm | Please refer reply against query no 79 |
|  |  | BPS, Schedule-1, sl. No. 48 | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length | We assume that there is the Provision/windows in the Existing FDA cum Annunciation panel located in the Existing Control Building to take the FDA Signal of Switchyard Panel Room . So New FDA panel at CRB is not required. Please confirm. | Confirmed |
|  |  | BPS, Schedule-1, sl. No. 48 | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length | We assume that there is Provision in the SCADA to have signals of AC system and Fire fighting system as per TS. pls confirm. | Bidder to Quote as per provision of bidding documents. |
|  |  | BPS, Schedule-1, sl. No. 48 | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length | Pls provide the exiting Fire fighting alarm system layout & SLD dwgs. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | BPS, Schedule-1, sl. No. 48 | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length | Pls provide the existing Indoor and outdoor cable trench layout dwg | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | BPS, Schedule-1, sl. No. 48 | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length | Pls provide the existing layout dwgs for locating the Control Building. | As Bikaner -II PS is being developed under separate package, the requisite details shall be provided during detailed engineering. Bidder shall quote as per BPS |
|  |  | TECHNICAL SPECIFICATION FOR FIRE FIGHTING SYSTEM & AIR CONDITIONING SYSTEM | General | We assume that there is Provision in the SCADA to have signals of AC system and Fire fighting system as per TS. pls confirm. | Bidder to Quote as per provision of bidding documents. |
|  |  | TECHNICAL SPECIFICATION FOR AIR CONDITIONING SYSTEM, | General | Air- Conditioning heat load calculation shall be done on the basis of max site temperature( 45 deg C) and unit will satisfactory work upto ambient temperature i.e. 50 deg Please confirm. | Bidder to Quote as per provision of bidding documents. |
|  |  | (Bhadla-II) |  |  |  |
|  |  | Section Project, Cl No. 3.1.c | Bus Protection : Any required modification in existing Busbar Protection of existing Main-I & Main-II for Protection and coordination with respect to sectionliser. | As per scope we will consider New bus bar protection for the sections created after Bus-Sectionalizer. However, for overlapping at Bus-section, 4 nos. of existing Busbar’s bay units are required. We understand that these (4 nos.) additional bay units (peripheral units) are not to be considered for Bus-sectionalizer Busbar Over-lapping. Existing bay units (spares due creation of new bus after Bus-Sectionalizer and supply of New busbar) shall be utilized by PGCIL, Please confirm. | As per section project clause no 3.1c) i. A “Supply & installation of New Busbar protections i.e. Redundant (1+1) numerical low impedance biased differential Bus Bar protection scheme for each Main bus i.e. both 400kV Main-I & Main-II bus sections which is created by Bus sectionaliser as per Section Control and Relay Panel of the Technical Specifications. Same shall be for all bays (Present, existing as well as future bays as shown in SLD) of section for which Busbar protection is provided by contractor.” It is further clarified that Dia1 to Dia8 & Bus sectionalizers shall be considered while finalising the total requirement of bay units for Bus bar Protection to be supplied under present scope. Further, after modification of existing bus bar protection for other section, 4nos spare PU units made available may be utilized for bus sectionalizer overlapping portion for existing Bus Bar protection only. However, all configuration etc. is to be done as per section project clause no 3.1. |
|  |  | Section Project : Cl No. 4.1 q) | These PMUs shall be integrated with Phasor data Concentrator (PDC) at LDC/SLDC for the subject project. | We understand that PMU integration with PDC is not in bidder’s scope. Scope is limited to configuration of PMU at substation end only required for integration with PDC. Please confirm. | Confirmed, however all the configuration work at substation end required for integration of PMU with PDC at RLDC/SLDC shall be in the scope of bidder |
|  |  | Test Certificates | Tender Submission | Kindly accept that the Test Certificates of individual Equipments as per tender can be submitted during detailed engineering after the award. | Noted |
|  |  | GTP | Tender Submission | Kindly accept that the GTP of individual Equipments as per tender can be submitted during detailed engineering after the award. | Noted |
|  |  | Bikaner-II - BPS S.No. 17 Sch-3 | Dismantling, transportation & re-erection of 400kV PLCC | Required supervsion will be arranged by PGCIL, also insuarnce for same equipment to be reimbursed at actuals, based on site cost estimate and age of equipments, as it is not supplied by us. We require OEMs supervsion if required and same will be arranged by PGCIL. Please confirm the same. | All the activities of dismantling, transportation, insurance and re-erection for 400 KV PLCC under supervision of OEM (if required) are in the scope of bidder and bidder to quote price in BPS item sl. No. 17 accordingly. |