| Sl. No | VOLUME/SEC No. | Clause No. |  | Bidder’s Query | POWERGRID Reply |
| --- | --- | --- | --- | --- | --- |
|  | General – 400kV GIS Chamera Substation |  |  | We did not see sufficient space for building GIS extension in layout drawing provided with bidding documents for 400kV GIS Chamera Substation. Please clarify if sufficient space is available at site | GIS Building extension is in present scope of work and as per owner estimate sufficient space for GIS Building extension is available at 400kV GIS Chamera Substation. However bidders are advised to visit Substation site in accordance to Clause No 3.4 of Section Project. |
|  | General – 400kV GIS Chamera Substation & 400kV Maharanibagh GIs substation |  |  | We request you to provide details of existing firefighting panel and existing layout drawing for FF system for Maharanibagh (GIS) Substation & 400kV Chamera Pooling Substation | Available major relevant drawings and details of existing old substation installations are enclosed with bidding documents. Other drawings & details, if available will be shared with the successful bidder during detailed engineering. However bidders are requested to visit the substation sites in accordance to clause no 3.4 of section project, technical specification. |
|  | General – 400kV GIS Chamera Substation & 400kV Maharanibagh GIs substation |  |  | We request you to provide details of existing LT switchgear for Maharanibagh (GIS) Substation & 400kV Chamera Pooling Substation | Available major relevant drawings and details of existing old substation installations are enclosed with bidding documents. Other drawings & details, if available will be shared with the successful bidder during detailed engineering. However bidders are requested to visit the substation sites in accordance to clause no 3.4 of section project, technical specification. |
|  | General – 400kV GIS Chamera Substation & 400kV Maharanibagh GIs substation |  |  | Kindly Provide SBC report for all substations | To be provided during detailed Engineering. |
|  | General – 400kV GIS Chamera Substation & 400kV Maharanibagh GIs substation |  |  | We presume that battery & battery charger present in all substations have sufficient capacity for extension work | Confirmed for Control & Relay requirement. Battery & Battery Charger have sufficient capacity for execution work. However in case driving mechanism of GIS equipment requires DC feed, any up gradation in Battery & Battery Charger is to be considered by Bidder as a part of GIS scope. |
|  | Schedule-3 of BPS- 2 Nos. of 400kV Line bays Chamera GIS |  |  | As per BPS, Sch-3, Sl. No 26 shows the requirement of 400kV Tower TH type but in supply schedule same is missing. Please confirm the requirement. | Please refer Amendment No.I. |
| Extension of 400KV Maharanibagh GIS Substation |  |  |  |  |  |
|  | As per section project clause- | 3.1.1-II-b |  | We understand, existing (RADHA, ABB Make) high impedance Bus Bar Protection scheme is absolute now and no support is being extended from ABB for the same. Kindly check with customer for replacement with new Centralized High/Low impedance Bus Bar Differential protection scheme. | Bidder to quote as per the Bidding Document. |
|  | As per section project clause- | 3.1.1-II-e |  | Please confirm provision of Integration(Module availability), No additional hardware required for Integration of Online.Please confirm | The existing PDM system is provided with capacity for readily interfacing with UHF PD couplers of upcoming GIS bays. However it is the responsibility of bidder to completely integrate the GIS bay under present scope with the existing PDM system. |
|  | CIVIL works |  |  | Kindly add line item of Pile foundation in BOQ for same. | The Line item for pile works already exists in the Bid Price Schedule. Bidder to quote as per Bid Price Schedule. |
|  | As per section project clause- | 3.1.1-II-b |  | We presume space available in existing Relay room of GIS hall. Please confirm | Please refer Clause 3.1.1 of Section Project where it is clearly mentioned that if due to design constraint, if GIS manufacturer is not able to accommodate Reactor bay in available space, cost of extension of GIS building may be included in module cost and nothing shall be paid separately on account of building extension. |
|  | As per section project clause- | 3.1.1-II-i |  | Please share existing details(Make & model) of Fire Fighting Annunciation system has to be augmented for present scope of work. | Available major relevant drawings and details of existing old substation installations are enclosed with bidding documents. Other drawings & details, if available will be shared with the successful bidder during detailed engineering. However bidders are requested to visit the substation sites in accordance to clause no 3.4 of section project, technical specification. |
|  | General queries |  |  | Please confirm if required please add line item for same. | Layout will be finalised during detailed Engineering. Bidder is requetsed to quote as per Bid Price Schedule |
| Extension of 400KV Chamera GIS Pooling Substation |  |  |  |  |  |
|  | As per section project clause- | 3.1.3-II-b | We understand, existing REB670 (ABB Make) Centralized Low impedance Bus Bar Differential Relay type have sufficient CT terminals for the present bay. No additional hardware/CT card are required.Please confirm |  | Existing Bus Bar protection is Centralized Low impedance Bus Bar Differential Relay type REB670 (ABB Make) , All the hardware for augmentation of 3 Nos. of bays is available and only scheme modification, supply of aux. relay, trip relay, cabling and wiring etc. as required, is in present scope. |
|  | Illumination System |  | Please confirm |  | LM is not envisaged. |
|  | As per BPS-1 Supply | Sr.43 | Please share existing details(Make & model) of Ventilation System. |  | Available major relevant drawings and details of existing old substation installations are enclosed with bidding documents. Other drawings & details, if available will be shared with the successful bidder during detailed engineering. However bidders are requested to visit the substation sites in accordance to clause no 3.4 of section project, technical specification. |
|  | As per section project clause- | 3.1.3-II-h | Please provide existing details make model of Fire Detection & Alarm System. |  | Available major relevant drawings and details of existing old substation installations are enclosed with bidding documents. Other drawings & details, if available will be shared with the successful bidder during detailed engineering. However bidders are requested to visit the substation sites in accordance to clause no 3.4 of section project, technical specification. |