## BOQ-Supply&F&I
SUBSTATION PACKAGE IN KENYA ON PPP-JV MODEL WITH AFRICA50
Substation Package – SS02 for 400/220 kV Lessos (complete) Substation under Transmission Line & Substation works associated with Transmission Project in Kenya through PPP-JV model with Africa50.
BILL OF QUANTITY
SUPPLY BOQ
Sl. No. | Description | Unit | Quantity | Unit Exwork Price | Remarks
I | 400/220kV Lessos Substation
I.i | Part-A : EMPLOYER ASSESSED QUANTITIES
A1 | POWER TRANSFORMER
1 | 500MVA, 400/220/33 KV, 3-phase Power Transformer excluding Insulating Oil | Nos | 2
2 | Insulating Oil for 500MVA, 400/220/33 KV, 3-phase Power Transformer | SET | 2
3 | DIGITAL RTCC PANEL | SET | 1
A2 | REACTORS
A2.1 | LINE REACTORS
(i) | 50 MVAR,420kV,3-phase Shunt Reactor excluding Insulating Oil | Nos. | 2
(ii) | Oil filled Neutral Grounding Reactor (NGR) along with support structure & terminal connector | Nos. | 2
(iii) | Insulating Oil for 50 MVAR,420kV ,3-phase Shunt Reactor | Set | 2
A2.2 | BUS REACTOR
(i) | 50 MVAR,420kV,3-phase Shunt Reactor excluding Insulating Oil | No. | 1
(ii) | Insulating Oil for 50 MVAR,420kV ,3-phase Shunt Reactor | Nos. | 1
A.3 | Testing & Maintenance Equipments
(i) | Oil Storage Tank (20kL) | No. | 2
(ii) | Transformer Oil Filtration plant (6KLPH) | No | 1
A.4 | LT TRANSFORMER
(i) | 630kVA, 33/0.433kV, 3ph Transformer | Nos | 2
B | 420 kV EQUIPMENT
i) | 420kV, 3150A, 40KA Circuit Breaker (3-Phase) with support structure without closing resistor | Nos | 10
ii) | Controlled Switching Device for 420 kV, 3-ph Circuit Breaker | EA | 4
iii) | 420kV, 3150A, 40 KA, 3-phase Double Break Isolator with one E/S | Nos | 22
iv) | 420kV, 3150A, 40 KA, 3-phase Double Break Isolator with two E/S | Nos | 2
v) | 420 kV, 3000A, 40KA, 1-Phase Current Transformer with 120% extended current rating | Nos | 24
vi) | 420 kV, 4400pf Capacitive Voltage Transformer (1- Phase) | Nos | 12
vii) | 336kV Surge Arrester (1-phase) | Nos | 21
viii) | 420 kV, 1 phase Bus Post Insulator (except for Line Traps) | Nos | 30
ix) | 420 kV ,1 phase Bus Post Insulators for Line Traps | Nos | 12
C | 245kV equipment
i) | 245kV, 2500A, 40KA Circuit Breaker (3-Phase) with support structure | Nos | 3
ii) | 245kV, 2500A, 40 KA, 3-phase Horizontal Centre Break (HCB) Isolator with one E/S | Nos | 2
iii) | 245kV, 2500A, 40 KA, 3-phase Horizontal Centre Break (HCB) with out E/S | Nos | 6
iv) | 245 kV, 2500A, 40KA, 1-Phase Current Transformer with 120% extended current rating | Nos | 24
v) | 245 kV, 4400pf Capacitive Voltage Transformer (1- Phase) | Nos | 6
vi) | 216kV Surge Arrester (1-phase) | Nos | 6
vii) | 245 kV, 1 phase Bus Post Insulator (except for Line Traps) | Nos | 30
D | 145kV outdoor Equipments
i) | 145kV, 1250A, 31.5KA Circuit Breaker (1-Phase) with support structure | Nos | 2
ii) | BPI (145kV) for NGR | Nos | 4
iii) | 120 kV Surge Arrester (1-Phase) | Nos | 2
E | 72.5kV outdoor Equipments (Tertiary Loading)
i) | 72.5 kV, 1250A, 25 kA, 3-phase CircuitBreaker with support structure | Nos | 1
ii) | 72.5 kV, 50A, 25 kA, 1-Phase CurrentTransformer with 120% extended currentrating | Nos | 3
iii) | 72.5 kV Voltage Transformer (1- Phase) | Nos | 3
iv) | 72.5 kV, 400A, 25 KA, 3-Phase DoubleBreak Isolator with out E/S | Nos | 1
v) | 72.5kV ,1 phase Bus Post Insulators | Nos | 9
F | 36kV outdoor Equipments
i) | 36 kV, 400A, 25 KA, 3-Phase HDB Isolatorwithout E/S | Nos | 1
ii) | 36 kV, 3-Ph Horn Gap Fuse as per Technical Specification | Nos | 1
iii) | 36kV, 1 phase Bus Post Insulators as per Technical Specification | Nos | 3
iv) | 30kV Surge Arrester (1-Phase) | Nos | 3
v) | Current transformer (33kV) for Reactor Neutral along with support structure & terminal connector | Nos | 2
G | RELAY PANELS (WITH AUTOMATION)
G1 | 400kV
i) | 400kV Circuit Breaker Relay Panel with Auto Reclose (with Automation) | Nos | 4
ii) | 400kV Circuit Breaker Relay Panel without Auto Reclose (with Automation) | Nos | 6
iii) | 400kV Transformer Protection Panel (For both HV & MV side)-(with Automation) | Nos | 2
iv) | 400kV Line Protection Panel (with Automation) | Nos | 2
v) | 400kV Reactor Protection Panel (with Automation) | Nos | 3
vi) | 400kV Bus Bar Protection Panel (Duplicate)-(with Automation) | SET | 1
G2 | 220kV
i) | 220kV Circuit Breaker Relay Panel with Auto Reclose (with Automation) | EA | 3
ii) | Augmentation of existing 220kV bus bar protection scheme.(No. of bays as per specification)-(with Automation) | Set | 1
H | COMMON EQUIPMENTS
i) | Relay tool kit as per Technical specification | Set | 1
ii) | Time synchronisation equipment | No. | 1
I | SUBSTATION AUTOMATION
I1 | 400kV
i) | Complete Substation automation System for 400kV Main bay as per Technical Specification | Nos | 5
ii) | Complete Substation automation System for 400kV Tie bay as per Technical Specification | Nos | 3
iii) | Complete Substation automation System for 400kV Switchable Line Reactor Bay as per Technical Specification | Nos | 2
iv) | Complete Substation automation System for controlling and monitoringof Auxilary System including BCUs as per technical specification | Set | 1
I1 | 220kV
i) | Complete Substation automation System for 220kV bay as per Technical Specification | Nos | 3
J | PLCC
J1 | PLCC AT LOCAL END
i) | 420kV, 3150A, 0.5mH, 40 kA Line Trap | Nos | 4
ii) | Coupling device for PLCC | SET | 2
iii) | Carrier Equipment Analog type (for Speech+Data & Speech+Protection) | Nos | 2
iv) | Protection Coupler for PLCC | Nos | 2
v) | Digital Protection Coupler | Nos | 2
vi) | HF CABLE 75 OHMS FOR PLCC | KM | 1
J2 | PLCC AT REMOTE END
i) | Coupling device for PLCC | SET | 2
ii) | Carrier Equipment Analog type (for Speech+Data & Speech+Protection) | Nos | 2
iii) | Protection Coupler for PLCC | Nos | 2
ix) | HF CABLE 75 OHMS FOR PLCC | KM | 1
iv) | Digital Protection Coupler | Nos | 2
J3 | Associated Communication Equipment at Local End
i) | EPAX (24/8) with 24 telephones, Cables etc. | SET | 1
ii) | 2 wire telephone equipment | Nos | 2
iii) | Testing & Maintenance equipment (print test kit only) for PLCC | SET | 1
K | LT Switchgear (As per Technical specification)
i) | 415V Main Switchboard | SET | 1
ii) | 415V AC Distribution Board (ACDB) as per Technical Specification | SET | 1
iii) | 415V Main Lighting DB (along with 2 nos. 100 kVA 415V/415V Lighting transformer) | SET | 1
iv) | 415V Emergency Lighting DB(along with 1 no. 50kVA 415V/415V lighting transformer) | SET | 1
v) | 220V DCDB | SET | 2
vi) | 48V DCDB | SET | 2
L | Batteries(The rating of batteries mentioned are minimum and shall be worked out by bidder as per Section Project, Technical Specification) & Battery Chargers
i) | 220V, 1200 Ah VRLA Battery | SET | 2
ii) | 220V, 150A/150A Float Cum Boost Battery Charger | Nos | 2
iii) | 48V, 1200Ah VRLA Battery | SET | 2
iv) | 48V, 150A/150A Float Cum Boost Battery Charger | Nos | 2
M | Diesel Generator with control Panel
i) | 250 kVA Diesel Generator along with AMF Panel | SET | 1
N | Illumination System
i) | Lighting Panel type ACP-2 as per technical specification | Nos | 6
ii) | Lighting Panel type ACP-3 as per technical specification | Nos | 3
iii) | Sub Lighting panel (outdoor) type SLP (Switchyard and Street Lighting) | Nos | 20
iv) | Lighting Fixture LED Luminaries Type FL-1 As per TS | Nos | 30
v) | Lighting Fixture LED Luminaries Type FL-2 As per TS | Nos | 60
vi) | 63A, 415V : Interlocked switch socket outdoor Receptacle (type RP) asper technical specifications | Nos | 3
vii) | Self Supported Aluminium Ladder as Per Technical Specification | Nos | 1
viii) | Cartwheel Mounted Aluminium Ladder as Per Technical Specification | Nos | 1
ix) | Outdoor Power Receptacle for oilfiltration unit (250A) | Nos | 3
x) | LED Street Light Luminaire Type SL-L1 (= 45W) As per TS | Nos | 30
xi) | Type L1 Street Lighting Pole of 6 Mtr as per TS | Nos | 30
xii) | Fire Wall mounted LED Luminarie Type FL-2 (250W) | Nos | 4
xiii) | Portable Flood Light Light Panel With LED Luminaries Type FL-2 (250W) | Nos | 2
xiv) | Type D1 Post Top Tantern Pole of 4mtr as per TS | Nos | 10
xv) | Pole Mounted LED Post Top Luminarie Type SL-D1 (= 30W) as per TS | Nos | 10
O | Fire Protection System
a | Portable /Trolley/Wheel mounted extinguishers
i) | 9 litre water type | Nos | 4
ii) | 60 litre foam type | Nos | 2
iii) | 4.5 kg CO2 type | Nos | 12
iv) | 4.5 kg Dry Chemical Power (DCP) type | Nos | 5
P | Air conditioning System for Control room cum administrative building & SPR
i) | High wall type split AC unit of 2 TR capacity | Nos | 15
Q | Lattice & Pipe structures
Q1 | 400kV Gantry Structures
i) | GANTRY STRUCTURE PER DIA-400KV - One and Half Breaker Layout | SET | 3
Q2 | 400kV Equipments Structures
i) | Equipment Structure Including Foundation bolts-400kV CT (1ph) | Nos | 24
ii) | Equipment Structure Including Foundation bolts-400kV CVT (1ph) | Nos | 12
iii) | Equipment Structure Including Foundation bolts-400kV Isolator (3Ph) | Nos | 24
iv) | Equipment Structure Including Foundation bolts-400kV Class SA (1ph) | Nos | 21
v) | Equipment Structure Including Foundation bolts-400kV BPI (1ph) | Nos | 30
vi) | Equipment Structure Including Foundation bolts-400kV Wave Trap (1ph) | Nos | 12
Q3 | 220kV Gantry Structures
i) | Gantry Structure for Transformer bay including bus work- 220 KV 3/4 Breaker Layout | SET | 2
i) | Gantry Structure for 2nos of Bus works (only) - 220 KV 3/4 Breaker Layout | SET | 2
Q4 | 220kV Equipments Structures
i) | Equipment Structure Including Foundation bolts-220kV CT (1ph) | EA | 24
ii) | Equipment Structure Including Foundation bolts-220kV CVT (1ph) | EA | 6
iii) | Equipment Structure Including Foundation bolts-220kV Isolator (3Ph) | EA | 8
iv) | Equipment Structure Including Foundation bolts-220kV Class SA (1ph) | EA | 6
v) | Equipment Structure Including Foundation bolts-220kV BPI (1ph) | EA | 20
vi) | Equipment Structure Including Foundation bolts-220kV High BPI (1ph) | EA | 10
Q5 | 145kV Equipments Structures
i) | Equipment Structure Including Foundation bolts-120kV SA (1ph) | Nos | 2
ii) | Equipment Structure Including Foundation bolts-145kV BPI (1ph) | Nos | 4
Q6 | 72.5 kV Equipments Structures
i) | Equipment Structure Including Foundation Bolt-72.5KV CT(1ph) | Nos | 3
ii) | Equipment Structure Including Foundation Bolt-72.5KV PT(1ph) | Nos | 3
iii) | Equipment Structure Including Foundation Bolt-72.5KV Isolator (3ph) | Nos | 1
iv) | Equipment Structure Including Foundation Bolt-72.5KV BPI(1ph) | Nos | 9
Q7 | 33kV Equipments Structures
i) | Equipment Structure including Foundation Bolts -36KV Isolator (3ph) | Nos | 1
ii) | Equipment Structure including Foundation Bolts-36KV Class SA (1ph) | Nos | 3
iii) | Equipment Structure including Foundation Bolts-36KV BPI (1ph) | Nos | 3
iv) | Equipment Structure including Foundation Bolts-36KV HG Fuse (1ph) | Nos | 3
Q.8 | NON-Standard Structures for 33kV line terminations
i) | Fabrication, galvanising and supply of Lattice Structures (MS Steel), to be designed during detailed engineering, for towers, beams and equipment support structure including pack plates / packwashers and gusset plates excluding fasteners and foundation bolts | MT | 12
ii) | Fabrication, galvanising and supply of fasteners ( nuts, bolts and washers ) including step bolts for lattice and pipe structures to be designed during detailed engineering | MT | 1
| Fabrication, galvanising and supply of foundation bolts including nuts, checknut and washers for lattice and pipe structures to be designed during detailed engineering | MT | 1
R | EHV Cables and accessaries
i) | 1Cx120sqmm, 33KV HV Power Cable along with accessories & cable terminations kit etc. | KM | 2
ii) | 1C x 2500Sqmm, Cu conductor, Lead sheath, XLPE, 220kV EHV Power Cable along with accessories etc. | KM | 2
iii) | 220kV Outdoor Cable End Terminations Suitable for 1Cx2500Sqmm XLPE Cables | SET | 12
iv) | Structures for 220kV Cable end termination(s) (1-Ph) as per Technical Specifications | SET | 12
S | VMS System
i) | Visual Monitoring System for Watch & Ward complete as per TS | Set | 1
T | Main Earth Mat
i) | 40 MM MS Rod for Main Earthmat | KM | 20
U | Telecom Equipments
1 | SDH Equipment (STM-16 MADM upto 5 MSP protected directions)
(i) | Base Equipment (Common cards, Cross Connect/control cards, optical base cards, power supply cards, power cabling, other hardware and accessories including sub racks, patch cord, DDF etc fully equiped excluding (ii) & (iii) below | Nos. | 1
(ii) | Optical Interface Cards/SFP
a | S4.1 | Nos. | 4
b | S16.1 | Nos. | 4
c | STM-4 OLIC to support 200 kms | Nos. | 2
d | STM-16 OLIC to support minimum 200 kms | Nos. | 2
(iii) | Tributary cards
a | E1 Interface card (Min.16 interfaces per card) | Nos. | 2
b | Ethernet Interface 10/100 Base T with Layer-2 switching (Min 8 Interfaces per card) | Nos. | 2
c | Gigabit Ethernet Interface# with Layer-2 switching (Minimum 2 nos.) | Set | 1
2 | Equipment Cabinets
a | For SDH | No. | 1
3 | Network Manager System
Craft Terminal
a | Hardware | Set## | 1
b | Software | Set## | 1
4 | VIOP Phone PLUS 8 Port SWITCH | No. | 4
Sub-Total Part-A
I.ii | Part-B: VENDOR ASSESSED QUANTITIES
A | Erection Hardware
A1 | 400kV
i) | Erection Hardware for 400kV I type layout-Bus Work (For one diameter) as per technical specification | SET | 3
ii) | Erection Hardware for 400kV I type layout-Line bay as per technical specification | SET | 2
iii) | Erection Hardware for 400kV I type layout-Line Reactor including NGR bypass arrangement as per technical specification | SET | 2
iv) | Erection Hardware for 400kV I type layout-Bus Reactor bay as per technical specification | SET | 1
v) | Erection Hardware for 400kV I type layout-Transformer bay as per technical specification | SET | 2
vi) | Erection Hardware for 400kV I type layout-Spare bay of half dia as per technical specification | SET | 1
A2 | 220kV
i) | Erection Hardware for 220kV layout (3/4 scheme)-Bus work (two Bay) as per technical specification | SET | 3
ii) | Erection Hardware for 220kV layout (3/4)-Transformer Bay as per technical specification | SET | 2
B | Uprating / Replacement of 2nos of 220 kV existing Main buses to 4000 A, 40 kA, 3 Secs rating complete as per TS | LOT | 1
C | Fire Protection System
i) | Pumping arrangement for HVW system & hydrant system, complete with all piping, valves, fittings,etc. inside pump house for Fire Protection System of 400/220kV (New) Substation | SET | 1
ii) | Hydrant system, complete U/G piping and accessories etc. outside the Pump House for Fire Protection of 400/220kV (New) Substation | SET | 1
iii) | HVW SPRAY SYSTEM, HYDRANT SYSTEM AND COMPLETE U/G & O/G PIPING AND ACCESSORIES ETC. OUT SIDE THE PUMP HOUSE FOR 420KV 3 PHASE BUS REACTOR | SET | 1
iv) | HVW SPRAY SYSTEM, HYDRANT SYSTEM AND COMPLETE U/G & O/G PIPING AND ACCESSORIES ETC. OUT SIDE THE PUMP HOUSE FOR 420KV 3 PHASE LINE REACTOR INCLUDING NGR | SET | 2
v) | HVW Spray System, hydrant System and Complete U/G & O/G piping and accessories etc. outside the pump house for 400kV 3ph Transformer | SET | 2
vi) | Fire Detection and Alarm System for Control Room Building (400kV) | SET | 1
vii) | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length | SET | 4
D | Illumination System
i) | Control room cum administrative building illumination | LS | 1
ii) | Fire fighting building illumination | LS | 1
iii) | Security Room Illumination including conduit | LS | 1
iv) | Transit Camp illumination | LS | 1
v) | Switchyard Panel room Lighting | LS | 4
vi) | Car parkings | LS | 1
vii) | Grid Interactive Solar PV Power Plant as per TS | LS | 1
E | Air conditioning & ventilation System
i) | Air conditioning system for Switchyard Panel Room of 6m length | SET | 4
F | POWER & CONTROL CABLES
i) | 1.1kV grade Power Cables (XLPE insulated)along with lugs,glands,straight joints & accessories , etc | LS | 1
ii) | 1.1kV grade Power Cables (PVC insulated)along with lugs,glands,straight joints & accessories , etc | LS | 1
iii) | 1.1kV grade Control Cables (PVC insulated)along with lugs,glands,straight joints & accessories , etc | LS | 1
Sub-Total Part-B
I.iii | Mandatory Spares
A | Mandatory Spares (S/s Portion)
i) | Spare-420kV Transformer | SET | 1
ii) | Spare-420kV Shunt Reactor | SET | 1
iii) | Spare-420kV Circuit Breaker | SET | 1
iv) | Spare-420kV Isolator | SET | 1
v) | Spare-420kV CT | SET | 1
vi) | Spare-420kV CVT | SET | 1
vii) | Spare-336kV SA | SET | 1
viii) | Spare-420kV BPI | Set | 1
ix) | Spare-245kV Circuit Breaker | SET | 1
x) | Spare-245kV Isolator | SET | 1
xi) | Spare-245kV CVT | SET | 1
xii) | Spare-245kV CT | SET | 1
xiii) | Spare-216kV LA | SET | 1
xiv) | Spare-245kV BPI | SET | 1
xv) | Relay & protection Panels (with automation) | LS | 1
xvi) | Spares-Substation Automation System | LS | 1
xvii) | Spare-PLCC | SET | 1
xviii) | Spares for DG set | LS | 1
xix) | Spares fpr 220V Battery Charger | LS | 1
xx) | Spares fpr 48V Battery Charger | LS | 1
xxi) | Spares for 220V Batteries | LS | 1
xxii) | Spares for 48V Batteries | LS | 1
xxiii) | SPARES FOR FIRE PROTECTION SYSTEM | SET | 1
xxiv) | SPARES FOR CLAMPS & CONNECTORS | LOT | 1
xxv) | SPARES FOR Power & Control Cable | LOT | 1
B | Mandatory Spares of Telecommunication Equipment
1) | SDH Equipment (STM-16 MADM upto 5 MSP protected directions)
a | Common cards, Cross-connect/control cards, Optical base card, Power supply cards, power cabling, other hardware & accessories (each). | Set$ | 1
2) | Optical Interface Cards/SFP
a | S4.1 | Nos. | 1
b | S16.1 | Nos. | 1
c | STM-4 OLIC to support 200 kms | Nos. | 1
d | STM-16 OLIC to support minimum 200 kms | Nos. | 1
3) | Tributary cards
a | E1 Interface card (Min.16 interfaces per card) | Nos. | 1
b | Ethernet Interface 10/100 Base T with Layer-2 switching (Min 8 Interfaces per card) | Nos. | 1
c | Gigabit Ethernet Interface# with Layer-2 switching (Minimum 2 nos.) | Set | 1
4 | VIOP Phone PLUS 8 Port SWITCH | No. | 1
5 | Pre Connectorized Optical Fiber Patch Cords(10 Mtrs) – Pack of six Patch cords | Set | 1
Sub-Total Part-C

## BOQ-Erection
SUBSTATION PACKAGE IN KENYA ON PPP-JV MODEL WITH AFRICA50
Substation Package – SS02 for 400/220 kV Lessos (complete) Substation under Transmission Line & Substation works associated with Transmission Project in Kenya through PPP-JV model with Africa50.
BILL OF QUANTITY
SERVICE BOQ
Sl. No. | Description | Unit | Quantity
I | 400/220kV Lessos Substation
I.i | Part-A : EMPLOYER ASSESSED QUANTITIES
A1 | POWER TRANSFORMER
1 | 500MVA, 400/220/33 KV, 3-phase Power Transformer excluding Insulating Oil | Nos | 2
2 | Insulating Oil for 500MVA, 400/220/33 KV, 3-phase Power Transformer | SET | 2
3 | DIGITAL RTCC PANEL | SET | 1
A2 | REACTORS
A2.1 | LINE REACTORS
(i) | 50 MVAR,420kV,3-phase Shunt Reactor excluding Insulating Oil | Nos. | 2
(ii) | Oil filled Neutral Grounding Reactor (NGR) along with support structure & terminal connector | Nos. | 2
(iii) | Insulating Oil for 50 MVAR,420kV ,3-phase Shunt Reactor | Set | 2
A2.2 | BUS REACTOR
(i) | 50 MVAR,420kV,3-phase Shunt Reactor excluding Insulating Oil | No. | 1
(ii) | Insulating Oil for 50 MVAR,420kV ,3-phase Shunt Reactor | Nos. | 1
A.3 | LT TRANSFORMER
(i) | 630kVA, 33/0.433kV, 3ph Transformer | Nos | 2
B | 420 kV EQUIPMENT
i) | 420kV, 3150A, 40KA Circuit Breaker (3-Phase) with support structure without closing resistor | Nos | 10
ii) | Controlled Switching Device for 420 kV, 3-ph Circuit Breaker | EA | 4
iii) | 420kV, 3150A, 40 KA, 3-phase Double Break Isolator with one E/S | Nos | 22
iv) | 420kV, 3150A, 40 KA, 3-phase Double Break Isolator with two E/S | Nos | 2
v) | 420 kV, 3000A, 40KA, 1-Phase Current Transformer with 120% extended current rating | Nos | 24
vi) | 420 kV, 4400pf Capacitive Voltage Transformer (1- Phase) | Nos | 12
vii) | 336kV Surge Arrester (1-phase) | Nos | 21
viii) | 420 kV, 1 phase Bus Post Insulator (except for Line Traps) | Nos | 30
ix) | 420 kV ,1 phase Bus Post Insulators for Line Traps | Nos | 12
C | 245kV equipment
i) | 245kV, 2500A, 40KA Circuit Breaker (3-Phase) with support structure | Nos | 3
ii) | 245kV, 2500A, 40 KA, 3-phase Horizontal Centre Break (HCB) Isolator with one E/S | Nos | 2
iii) | 245kV, 2500A, 40 KA, 3-phase Horizontal Centre Break (HCB) with out E/S | Nos | 6
iv) | 245 kV, 2500A, 40KA, 1-Phase Current Transformer with 120% extended current rating | Nos | 24
v) | 245 kV, 4400pf Capacitive Voltage Transformer (1- Phase) | Nos | 6
vi) | 216kV Surge Arrester (1-phase) | Nos | 6
vii) | 245 kV, 1 phase Bus Post Insulator (except for Line Traps) | Nos | 30
D | 145kV outdoor Equipments
i) | 145kV, 1250A, 31.5KA Circuit Breaker (1-Phase) with support structure | Nos | 2
ii) | BPI (145kV) for NGR | Nos | 4
iii) | 120 kV Surge Arrester (1-Phase) | Nos | 2
E | 72.5kV outdoor Equipments (Tertiary Loading)
i) | 72.5 kV, 1250A, 25 kA, 3-phase CircuitBreaker with support structure | Nos | 1
ii) | 72.5 kV, 50A, 25 kA, 1-Phase CurrentTransformer with 120% extended currentrating | Nos | 3
iii) | 72.5 kV Voltage Transformer (1- Phase) | Nos | 3
iv) | 72.5 kV, 400A, 25 KA, 3-Phase DoubleBreak Isolator with out E/S | Nos | 1
v) | 72.5kV ,1 phase Bus Post Insulators | Nos | 9
F | 36kV outdoor Equipments
i) | 36 kV, 400A, 25 KA, 3-Phase HDB Isolatorwithout E/S | Nos | 1
ii) | 36 kV, 3-Ph Horn Gap Fuse as per Technical Specification | Nos | 1
iii) | 36kV, 1 phase Bus Post Insulators as per Technical Specification | Nos | 3
iv) | 30kV Surge Arrester (1-Phase) | Nos | 3
v) | Current transformer (33kV) for Reactor Neutral along with support structure & terminal connector | Nos | 2
G | RELAY PANELS (WITH AUTOMATION)
G1 | 400kV
i) | 400kV Circuit Breaker Relay Panel with Auto Reclose (with Automation) | Nos | 4
ii) | 400kV Circuit Breaker Relay Panel without Auto Reclose (with Automation) | Nos | 6
iii) | 400kV Transformer Protection Panel (For both HV & MV side)-(with Automation) | Nos | 2
iv) | 400kV Line Protection Panel (with Automation) | Nos | 2
v) | 400kV Reactor Protection Panel (with Automation) | Nos | 3
vi) | 400kV Bus Bar Protection Panel (Duplicate)-(with Automation) | SET | 1
G2 | 220kV
i) | 220kV Circuit Breaker Relay Panel with Auto Reclose (with Automation) | EA | 3
ii) | Augmentation of existing 220kV bus bar protection scheme.(No. of bays as per specification)-(with Automation) | Set | 1
H | COMMON EQUIPMENTS
i) | Time synchronisation equipment | No. | 1
I | SUBSTATION AUTOMATION
I1 | 400kV
i) | Complete Substation automation System for 400kV Main bay as per Technical Specification | Nos | 5
ii) | Complete Substation automation System for 400kV Tie bay as per Technical Specification | Nos | 3
iii) | Complete Substation automation System for 400kV Switchable Line Reactor Bay as per Technical Specification | Nos | 2
iv) | Complete Substation automation System for controlling and monitoringof Auxilary System including BCUs as per technical specification | Set | 1
I1 | 220kV
i) | Complete Substation automation System for 220kV bay as per Technical Specification | Nos | 3
J | PLCC
J1 | PLCC AT LOCAL END
i) | 420kV, 3150A, 0.5mH, 40 kA Line Trap | Nos | 4
ii) | Coupling device for PLCC | SET | 2
iii) | Carrier Equipment Analog type (for Speech+Data & Speech+Protection) | Nos | 2
iv) | Protection Coupler for PLCC | Nos | 2
v) | Digital Protection Coupler | Nos | 2
vi) | HF CABLE 75 OHMS FOR PLCC | KM | 1
J2 | PLCC AT REMOTE END
i) | Coupling device for PLCC | SET | 2
ii) | Carrier Equipment Analog type (for Speech+Data & Speech+Protection) | Nos | 2
iii) | Protection Coupler for PLCC | Nos | 2
ix) | HF CABLE 75 OHMS FOR PLCC | KM | 1
iv) | Digital Protection Coupler | Nos | 2
J3 | Associated Communication Equipment at Local End
i) | EPAX (24/8) with 24 telephones, Cables etc. | SET | 1
ii) | 2 wire telephone equipment | Nos | 2
iii) | Testing & Maintenance equipment (print test kit only) for PLCC | SET | 1
K | LT Switchgear (As per Technical specification)
i) | 415V Main Switchboard | SET | 1
ii) | 415V AC Distribution Board (ACDB) as per Technical Specification | SET | 1
iii) | 415V Main Lighting DB (along with 2 nos. 100 kVA 415V/415V Lighting transformer) | SET | 1
iv) | 415V Emergency Lighting DB(along with 1 no. 50kVA 415V/415V lighting transformer) | SET | 1
v) | 220V DCDB | SET | 2
vi) | 48V DCDB | SET | 2
L | Batteries(The rating of batteries mentioned are minimum and shall be worked out by bidder as per Section Project, Technical Specification) & Battery Chargers
i) | 220V, 1200 Ah VRLA Battery | SET | 2
ii) | 220V, 150A/150A Float Cum Boost Battery Charger | Nos | 2
iii) | 48V, 1200Ah VRLA Battery | SET | 2
iv) | 48V, 150A/150A Float Cum Boost Battery Charger | Nos | 2
M | Diesel Generator with control Panel
i) | 250 kVA Diesel Generator along with AMF Panel | SET | 1
N | Illumination System
i) | Lighting Panel type ACP-2 as per technical specification | Nos | 6
ii) | Lighting Panel type ACP-3 as per technical specification | Nos | 3
iii) | Sub Lighting panel (outdoor) type SLP (Switchyard and Street Lighting) | Nos | 20
iv) | Lighting Fixture LED Luminaries Type FL-1 As per TS | Nos | 30
v) | Lighting Fixture LED Luminaries Type FL-2 As per TS | Nos | 60
vi) | 63A, 415V : Interlocked switch socket outdoor Receptacle (type RP) asper technical specifications | Nos | 3
vii) | Outdoor Power Receptacle for oilfiltration unit (250A) | Nos | 3
viii) | LED Street Light Luminaire Type SL-L1 (= 45W) As per TS | Nos | 30
ix) | Type L1 Street Lighting Pole of 6 Mtr as per TS | Nos | 30
x) | Fire Wall mounted LED Luminarie Type FL-2 (250W) | Nos | 4
xi) | Portable Flood Light Light Panel With LED Luminaries Type FL-2 (250W) | Nos | 2
xii) | Type D1 Post Top Tantern Pole of 4mtr as per TS | Nos | 10
xiii) | Pole Mounted LED Post Top Luminarie Type SL-D1 (= 30W) as per TS | Nos | 10
O | Fire Protection System
a | Portable /Trolley/Wheel mounted extinguishers
i) | 9 litre water type | Nos | 4
ii) | 60 litre foam type | Nos | 2
iii) | 4.5 kg CO2 type | Nos | 12
iv) | 4.5 kg Dry Chemical Power (DCP) type | Nos | 5
P | Air conditioning System for Control room cum administrative building & SPR
i) | High wall type split AC unit of 2 TR capacity | Nos | 15
Q | Lattice & Pipe structures
Q1 | 400kV Gantry Structures
i) | GANTRY STRUCTURE PER DIA-400KV - One and Half Breaker Layout | SET | 3
Q2 | 400kV Equipments Structures
i) | Equipment Structure Including Foundation bolts-400kV CT (1ph) | Nos | 24
ii) | Equipment Structure Including Foundation bolts-400kV CVT (1ph) | Nos | 12
iii) | Equipment Structure Including Foundation bolts-400kV Isolator (3Ph) | Nos | 24
iv) | Equipment Structure Including Foundation bolts-400kV Class SA (1ph) | Nos | 21
v) | Equipment Structure Including Foundation bolts-400kV BPI (1ph) | Nos | 30
vi) | Equipment Structure Including Foundation bolts-400kV Wave Trap (1ph) | Nos | 12
Q3 | 220kV Gantry Structures
i) | Gantry Structure for Transformer bay including bus work- 220 KV 3/4 Breaker Layout | SET | 2
i) | Gantry Structure for 2nos of Bus works (only) - 220 KV 3/4 Breaker Layout | SET | 2
Q4 | 220kV Equipments Structures
i) | Equipment Structure Including Foundation bolts-220kV CT (1ph) | EA | 24
ii) | Equipment Structure Including Foundation bolts-220kV CVT (1ph) | EA | 6
iii) | Equipment Structure Including Foundation bolts-220kV Isolator (3Ph) | EA | 8
iv) | Equipment Structure Including Foundation bolts-220kV Class SA (1ph) | EA | 6
v) | Equipment Structure Including Foundation bolts-220kV BPI (1ph) | EA | 20
vi) | Equipment Structure Including Foundation bolts-220kV High BPI (1ph) | EA | 10
Q5 | 145kV Equipments Structures
i) | Equipment Structure Including Foundation bolts-120kV SA (1ph) | Nos | 2
ii) | Equipment Structure Including Foundation bolts-145kV BPI (1ph) | Nos | 4
Q6 | 72.5 kV Equipments Structures
i) | Equipment Structure Including Foundation Bolt-72.5KV CT(1ph) | Nos | 3
ii) | Equipment Structure Including Foundation Bolt-72.5KV PT(1ph) | Nos | 3
iii) | Equipment Structure Including Foundation Bolt-72.5KV Isolator (3ph) | Nos | 1
iv) | Equipment Structure Including Foundation Bolt-72.5KV BPI(1ph) | Nos | 9
Q7 | 33kV Equipments Structures
i) | Equipment Structure including Foundation Bolts -36KV Isolator (3ph) | Nos | 1
ii) | Equipment Structure including Foundation Bolts-36KV Class SA (1ph) | Nos | 3
iii) | Equipment Structure including Foundation Bolts-36KV BPI (1ph) | Nos | 3
iv) | Equipment Structure including Foundation Bolts-36KV HG Fuse (1ph) | Nos | 3
Q.8 | NON-Standard Structures for 33kV line terminations
i) | Erection of Lattice Structures (MS Steel), to be designed during detailed engineering, for towers, beams and equipment support structure including pack plates / packwashers and gusset plates excluding fasteners and foundation bolts | MT | 12
ii) | Erection of fasteners ( nuts, bolts and washers ) including step bolts for lattice and pipe structures to be designed during detailed engineering | MT | 1
ii) | Erection of foundation bolts including nuts, checknut and washers for lattice and pipe structures to be designed during detailed engineering | MT | 1
R | EHV Cables and accessaries
i) | 1Cx120sqmm, 33KV HV Power Cable along with accessories & cable terminations kit etc. | KM | 2
ii) | 1C x 2500Sqmm, Cu conductor, Lead sheath, XLPE, 220kV EHV Power Cable along with accessories etc. | KM | 2
iii) | 220kV Outdoor Cable End Terminations Suitable for 1Cx2500Sqmm XLPE Cables | SET | 12
iv) | Structures for 220kV Cable end termination(s) (1-Ph) as per Technical Specifications | SET | 12
S | VMS System
i) | Visual Monitoring System for Watch & Ward complete as per TS | Set | 1
T | Main Earth Mat
i) | 40 MM MS Rod for Main Earthmat | KM | 20
U | Telecom Equipments
1 | SDH Equipment (STM-16 MADM upto 5 MSP protected directions)
(i) | Base Equipment (Common cards, Cross Connect/control cards, optical base cards, power supply cards, power cabling, other hardware and accessories including sub racks, patch cord, DDF etc fully equiped excluding (ii) & (iii) below | Nos. | 1
(ii) | Optical Interface Cards/SFP
a | S4.1 | Nos. | 4
b | S16.1 | Nos. | 4
c | STM-4 OLIC to support 200 kms | Nos. | 2
d | STM-16 OLIC to support minimum 200 kms | Nos. | 2
(iii) | Tributary cards
a | E1 Interface card (Min.16 interfaces per card) | Nos. | 2
b | Ethernet Interface 10/100 Base T with Layer-2 switching (Min 8 Interfaces per card) | Nos. | 2
c | Gigabit Ethernet Interface# with Layer-2 switching (Minimum 2 nos.) | Set | 1
2 | Equipment Cabinets
a | For SDH | No. | 1
3 | Network Manager System
Craft Terminal
a | Hardware | Set## | 1
b | Software | Set## | 1
4 | VIOP Phone PLUS 8 Port SWITCH | No. | 4
V | Civil Works (as per Technical Specification)
1 | Excavation in all kind of soil including rock for all leads and lifts, backfilling, disposal of surplus earth within a lead up to 2 Km as per technical specification. The surplus earth shall be roughly graded. | CUM | 21843
2 | Providing and laying of Plain Cement Concrete (PCC) (1:4:8) | CUM | 1447
3 | Providing and laying of Plain Cement Concrete (PCC) (1:2:4) | CUM | 318
4 | Providing and laying of Plain Cement Concrete (PCC) (1:3:6) | CUM | 15
5 | Providing and laying Plain Cement Concrete 1:5:10 | CUM | 6120
6 | Providing and laying of Reinforced Cement Concrete as per Technical Specification including pre cast, shuttering, Grouting of pockets & underpinning but excluding steel reinforcemen | CUM | 7122
7 | Steel Reinforcement | MT | 499
8 | Stone filling (40 mm size) for transformer/ reactor foundation | CUM | 84
9 | Misc. Structural steel including rails, embedments, edge protection angles, gratings etc. but excluding the reinforcement steel and steel for lattice and pipe structures. | MT | 142
10 | Stone spreading in switchyard excluding PCC | SQM | 80000
11 | Antiweed treatment | SQM | 80000
12 | External finishing/painting of firewall (with water proofing cement paint) | SQM | 720
13 | 3.75m wide Cement Concrete road with PCC shoulder including 100 mm dia RCC Hume Pipe @ 100 metre interval as per drawing and TS. However, reinforcement steel and all type concrete shall be paid separately under relevant items | SQM | 3000
14 | 5.5m wide Cement Concrete road with PCC shoulder including 100 mm dia RCC Hume Pipe @ 100 metre interval as per drawing and TS. However, reinforcement steel and and all type concrete shall be paid separately under relevant items | SQM | 750
15 | Construction of rail cum road as per drawing including all item such as excavation,compactions, rolling watering, WBM etc. but excluding concrete reinforcement and structural steel-Section having four rails for auto transformer. | SQM | 185
16 | Construction of rail cum road as per drawing including all item such as excavation,compactions, rolling watering, WBM etc. but excluding concrete reinforcement and structural steel-Section having two rails for Reactor. | SQM | 203
17 | Supplying and erecting dewatering pumps- 2 HP | Nos. | 2
18 | Supplying and erecting dewatering pumps-5 HP | Nos. | 5
19 | New chain Link Fencing excluding concrete | RM | 800
20 | Switchyard Gate excluding Concrete | Nos. | 2
21 | Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required. : 150 mm dia | RM | 30
22 | Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required. : 250 mm dia | RM | 135
23 | RCC culverts and cable trench crossings including supplying and laying hume pipe 250mm dia of grade (NP-3) excluding concrete as per specification. | RM | 30
24 | RCC culverts and cable trench crossings including supplying and laying hume pipe 300mm dia of grade (NP-3) excluding concrete as per specification. | RM | 30
25 | RCC culverts and cable trench crossings including supplying and laying hume pipe 450mm dia of grade (NP-3) excluding concrete as per specification. | RM | 30
26 | Drain including culverts but excluding concrete & reinforcement steel-Section A-A | RM | 1200
27 | Drain including culverts but excluding concrete & reinforcement steel-Section B-B | RM | 600
28 | Drain including culverts but excluding concrete & reinforcement steel-Section C-C | RM | 200
29 | Drain including culverts but excluding concrete & reinforcement steel-Section D-D | RM | 200
30 | Rain water harvesting excluding reinforcement and concrete as per drawing | Nos. | 2
31 | Control room building excluding excavation, PCC, RCC and reinforcement but including finishing ( internal + external ) & all civil works etc complete in all respect as per drawing. | SQM | 750
32 | FFPH Building - Civil Works All civil works as per drawing and specifications complete, including - brickwork,finishing (external and internal),windows etc.However, excavation, PCC,RCC and reinforcement shall be paid separately as per BPS | SQM | 101
33 | All civil works as per drawing and specification but excluding excavation, PCC, RCC, reinforcement but including finishing (internal and external) etc & all civil works complete in all respect - Water Tank for Fire Fighting Pump House | Nos. | 1
34 | "Switchyard Panel Room - Civil Works. All civil works as per drawing and specifications complete, including - brickwork, finishing (external and internal), windows etc. However, excavation, PCC, RCC and reinforcement shall be paid separately as per BPS." | SQM | 121
35 | Transit Camp - Civil Works All civil works as per drawing and specifications complete, including - brickwork, finishing (external and internal), windows etc. However, excavation, PCC, RCC and reinforcement shall be paid separately as per BPS. | SQM | 450
36 | Design, Drawing and execution of Pre-fabricated structure labour Hut including toilet & baths with all materials, labours etc complete in all respect as per the technical specification and direction of Engineer â€“ in Charge. (Plinth area shall be measured for payment purpose) | SQM | 420
37 | Security Hut - Civil Works All civil works as per drawing and specifications complete, including - brickwork, finishing (external and internal), windows etc. However, excavation, PCC, RCC and reinforcement shall be paid separately as per BPS. | SQM | 18
38 | Main Gate | Nos. | 1
39 | "Car Parking (8 cars) - Civil Works. All civil works as per drawing and specifications complete, including - brickwork,xiii) Carparking Shed (For 8 Cars) finishing (external and internal), windows etc.However,excavation, PCC, RCC and reinforcement shall be paid separately as per BPS." | SQM | 120
40 | Closed Store: Design preparation of drawings, supply of all materials, fabrication, erection & commissioning of Store Building. The work includes design and construction of foundations, plinth beams, brickwork, external & internal finishing, floor finishing, doors, windows, rolling shutters etc. complete in all respects as per the approved design, drawings and Technical specifications. However, excavation, PCC, RCC and reinforcement shall be paid under relevant item of BPS. | SQM | 360
41 | Partially Closed Store: Design preparation of drawings, supply of all materials, fabrication, erection & commissioning of Store Building. The work includes design and construction of foundations, plinth beams, brickwork, external & internal finishing, floor finishing, doors, windows, rolling shutters etc. complete in all respects as per the approved design, drawings and Technical specifications. However, excavation, PCC, RCC and reinforcement shall be paid under relevant item of BPS. | SQM | 360
42 | Providing and fixing Pre cast RCC Boundary wall as per drawings and specifications, including centring, shuttering, moulding,RCC, reinforcement, casting, curing, hoisting, carriage of precast cols/panels to site,Excavation, PCC, backfilling, steel gratings at required locations, MS angles and Concertina coil etc. complete. | RM | 1600
43 | Supplying and laying CPVC pipe for external water supply system - 75 mm dia pipe | RM | 200
44 | Supplying and laying CPVC pipe for external water supply system - 50 mm dia pipe | RM | 150
45 | Supplying and laying CPVC pipe for external water supply system - 40 mm dia pipe | RM | 150
46 | Supplying and laying CPVC pipe for external water supply system - 25 mm dia pipe | RM | 150
47 | SEPTIC TANK AND SOAKPIT FOR CRB | Nos. | 1
48 | SEPTIC TANK & SOAKPIT FOR SECURITY ROOM | Nos. | 1
49 | SEPTIC TANK AND SOAKPIT - TRANSIT CAMP | Nos. | 1
50 | Providing & Laying of SW pipes for external sewerage system as per technical specification 100mm dia pipe | RM | 100
51 | Providing & Laying of SW pipes for external sewerage system as per technical specification 150mm dia pipe | RM | 100
52 | Providing & Laying of SW pipes for external sewerage system as per technical specification 200mm dia pipe | RM | 80
53 | Soil Investigation: As per technical specification including all laboratory and field tests, report and recommendations. | LOT | 1
54 | Earthwork in excavation in all types of soils in open areas/nallas/ channels, to the required slopes, shapes, levels, elevations and profile, including trimming of bottom and slopes of excavation, bailing out rain (dewatering), pumping, removal of slush, and disposal of soil for lead up to one Kilometer and all lifts, with all labour, material, tools, tackles and equipment, safeguards and incidentals, as necessary, as per drawings, specification and directions of the Engineer-in-Charge.on and directions of the Engineer-in-Charge. | CUM | 100000
55 | Supply of earth (excluding rock & boulders) at site including royalty,carriage and filling in specified areas in layers not exceeding 200mm in depth, compacting under optimum moisture condition to achieve 95% of Proctor density,finishing etc. all complete, for all leads & lifts, with all labour, material, tools, tackles, equipments, safeguards & incidentals as necessary as per drawings, specification and direction of the Engineer- in- Charge. | CUM | 50000
56 | Dry stone pitching 22.5 cm thick including supply of stones and preparing surface complete. | SQM | 1342
57 | Supplying, filling and compacting stone boulders mixed with sand under foundations, roads, cable trenches, drains etc in layers not exceeding 250mm thickness including ramming, watering, compacting etc | CUM | 473
Sub-Total Part-A
I.ii | Part-B: VENDOR ASSESSED QUANTITIES
A | Erection Hardware
A1 | 400kV
i) | Erection Hardware for 400kV I type layout-Bus Work (For one diameter) as per technical specification | SET | 3
ii) | Erection Hardware for 400kV I type layout-Line bay as per technical specification | SET | 2
iii) | Erection Hardware for 400kV I type layout-Line Reactor including NGR bypass arrangement as per technical specification | SET | 2
iv) | Erection Hardware for 400kV I type layout-Bus Reactor bay as per technical specification | SET | 1
v) | Erection Hardware for 400kV I type layout-Transformer bay as per technical specification | SET | 2
vi) | Erection Hardware for 400kV I type layout-Spare bay of half dia as per technical specification | SET | 1
A2 | 220kV
i) | Erection Hardware for 220kV layout (3/4 scheme)-Bus work (two Bay) as per technical specification | SET | 3
ii) | Erection Hardware for 220kV layout (3/4)-Transformer Bay as per technical specification | SET | 2
B | Uprating / Replacement of 2nos of 220 kV existing Main buses to 4000 A, 40 kA, 3 Secs rating complete as per TS | LOT | 1
C | Fire Protection System
i) | Pumping arrangement for HVW system & hydrant system, complete with all piping, valves, fittings,etc. inside pump house for Fire Protection System of 400/220kV (New) Substation | SET | 1
ii) | Hydrant system, complete U/G piping and accessories etc. outside the Pump House for Fire Protection of 400/220kV (New) Substation | SET | 1
iii) | HVW SPRAY SYSTEM, HYDRANT SYSTEM AND COMPLETE U/G & O/G PIPING AND ACCESSORIES ETC. OUT SIDE THE PUMP HOUSE FOR 420KV 3 PHASE BUS REACTOR | SET | 1
iv) | HVW SPRAY SYSTEM, HYDRANT SYSTEM AND COMPLETE U/G & O/G PIPING AND ACCESSORIES ETC. OUT SIDE THE PUMP HOUSE FOR 420KV 3 PHASE LINE REACTOR INCLUDING NGR | SET | 2
v) | HVW Spray System, hydrant System and Complete U/G & O/G piping and accessories etc. outside the pump house for 400kV 3ph Transformer | SET | 2
vi) | Fire Detection and Alarm System for Control Room Building (400kV) | SET | 1
vii) | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length | SET | 4
D | Illumination System
i) | Control room cum administrative building illumination | LS | 1
ii) | Fire fighting building illumination | LS | 1
iii) | Security Room Illumination including conduit | LS | 1
iv) | Transit Camp illumination | LS | 1
v) | Switchyard Panel room Lighting | LS | 4
vi) | Car parkings | LS | 1
vii) | Grid Interactive Solar PV Power Plant as per TS | LS | 1
E | Air conditioning & ventilation System
i) | Air conditioning system for Switchyard Panel Room of 6m length | SET | 4
F | POWER & CONTROL CABLES
i) | 1.1kV grade Power Cables (XLPE insulated)along with lugs,glands,straight joints & accessories , etc | LS | 1
ii) | 1.1kV grade Power Cables (PVC insulated)along with lugs,glands,straight joints & accessories , etc | LS | 1
iii) | 1.1kV grade Control Cables (PVC insulated)along with lugs,glands,straight joints & accessories , etc | LS | 1
Sub-Total Part-B